## Sheet1
no | Eng | Picture | Option_1_Eng | Option_2_Eng | Option_3_Eng | Option_4_Eng | Ans | Vocab | Jpn | Option_1_Jpn | Option_2_Jpn | Option_3_Jpn | Option_4_Jpn | Exp | comment
1 | There are two copper wires of the same material, A and B. A is 1.6[mm] in diameter and 40[m] in length, and B is 3.2[mm] in diameter and 20[m] in length. How many times is the resistance of A greater than the resistance of B? |  | 2 | 4 | 6 | 8 | 4 | ['抵抗(ていこう)- Resistance', '直径(ちょっけい)- Diameter', '銅線(どうせん)- Copper line', '材質(ざいしつ) - Material'] | A,B2本の同{材質}の{銅線}がある。Aは{直径}1.6[mm],{長さ}40[m],Bは{直径}3.2[mm],{長さ}20[m]である。Aの抵抗はBの抵抗の何倍か。 | 2 | 4 | 6 | 8 | The cross-sectional area of ​​A is 0.8*0.8*π＝0.64π The cross-sectional area of ​​B is 1.6*1.6*π＝2.56π Therefore, the cross-sectional area of ​​A is 1/4 that of B Also, the length of A is 40m and the length of B is 20m, so the length of A is twice as long as B. Therefore, 4 times x 2 times = 8 times | 2011_1,
2 | In the circuit shown in the figure, when the switch S is closed, the voltage [V] between terminals a and b is ? | Picture_2 | 20 | 40 | 50 | 60 | 4 | ['電圧(でんあつ)- Voltage', '回路(かいろ)- Circuit'] | {図}のような{回路}で、{スイッチ}Sを閉じたとき、a-b{端子}間の{電圧}[V]は。 | 20 | 40 | 50 | 60 | R = 30Ω + 30Ω = 60Ω. I ＝V/R = 100/60 V ＝I×R = (100/60)×30= 50 | 2011_1,
3 | What is the calorific value [kJ] when an electric heater with a power consumption of 300 [W] is used for 2 hours? |  | 36 | 600 | 1080 | 2160 | 4 | ['発熱量(はつねつりょう)- Calorific value', '電熱器(でんねつき)- Electrothermic equipment'] | 消費{電力}が300[W]の{電熱器}を、2時間{使用}したときの{発熱量}[kJ]は。 | 36 | 600 | 1080 | 2160 | ​​1W = 3600J J = Ws, J = 300W x 2 hours = 600, 600 x 3600 = 2160000J = 2160kJ. | 2011_1,
4 | The formula for the power factor [%] of the AC circuit shown in the figure is | Picture_4 | Picture_4_A | Picture_4_B | Picture_4_C | Picture_4_D | 1 | ['力率(りきりつ)- Power factor', '交流(こうりゅう)- Exchange'] | {図}のような{交流}{回路}の{力率}[%]を{示す}式は。 | Picture_4_A | Picture_4_B | Picture_4_C | Picture_4_D | Also, since it is a formula that shows the power factor (%), it is also a point that it is 100R. | 2011_1,
5 | In a three-phase three-wire circuit with a power supply voltage E [V] as shown in the figure, if the wire is broken at the point marked with an x, the current I [A] flowing through the resistance R [Ω] between a and b after the wire breakage is: | Picture_5 | E/2R | E/√3R | E/R | 3E/2R | 1 | ['回路(かいろ)- Circuit', '電源(でんげん)- Ectrical power'] | {図}のような{電源}{電圧}E[V]の{三相}3線式{回路}で、×印点で{断線}すると、{断線}後のa-b間の抵抗R[Ω]に{流れる}{電流}I[A]は。 | E/2R | E/√3R | E/R | 3E/2R | From the basic I=E/R, by breaking the wire, it becomes I=E/(R+R) and becomes I=E/2R | 2011_1,
6 | In low-voltage indoor wiring work using metal pipes, if four 600V vinyl insulated wires (annealed copper wires) with a diameter of 1.6 mm are inserted into the pipe, what is the allowable current [A] per wire? However, the ambient temperature should be 30[°C] or less, and the current reduction factor should be 0.63. |  | 15 | 17 | 19 | 27 | 2 | ['電線(でんせん)- electric cable', '場合(ばあい)- Situation', '管内(かんない)- In a pipe', '低圧(ていあつ)- Low voltage'] | {金属}管による{低圧}{屋内配線}{工事}で、{管内}に{直径}1.6[mm]の600Vビニル{絶縁}{電線}（軟{銅線}）4本を挿入して{施設}した{場合}、{電線}1本{当たり}の{許容}{電流}[A]は。 ただし、{周囲}{温度}は30[℃]{以下}、{電流}{減少}{係数}は0.63とする。 | 15 | 17 | 19 | 27 | Allowable current is 1.6mm diameter = 27A , 2.0mm diameter = 35A , 2.6mm diameter = 48A The allowable current is 27×0.63=17[A]. | 2011_1,
7 | In the single-phase two-wire circuit shown in the figure, when the voltage between c-c' is 100[V], the voltage [V] between a-a' is: However, r is the electrical resistance [Ω] of the wire. | Picture_7 | 102 | 103 | 104 | 105 | 2 | ['電圧(でんあつ)- Volatage', '回路(かいろ)- Circuit'] | {図}のような{単相}2線式{回路}で、c-c’間の{電圧}が100[V]のとき、a-a’間の{電圧}[V]は。 ただし、ｒは{電線}の{電気}抵抗[Ω]とする。 | 102 | 103 | 104 | 105 | V(ab) = 10 [A] x 0.1 [Ω] = 1 [V] V (a'b') = 10 [A] x 0.1 [Ω] = 1 [V] V(bc) = 5[A] x 0.1[Ω] = 0.5[V] V(b'c') = 5[A] x 0.1[Ω] = 0.5[V] V (a-a') = 100 + V (ab) + V (a'b') + V (bc) + V (b'c') = 100 + 1 + 1 + 0.5 + 0.5 = 103[V] | 2011_1,
8 | In a three-phase three-wire circuit as shown in the figure, when the resistance per wire is 0.1 [Ω] and the wire current is 20 [A], the power loss [W] in this wire line is: | Picture_8 | 40 | 80 | 100 | 120 | 4 | ['抵抗(ていこう)- Resistor', '三相(さんそう)- Three phases'] | {図}のような{三相}3線式{回路}で、{電線}1線{当たり}の抵抗が0.1[Ω]、線{電流}が20[A]のとき、この{電線}路の{電力}損失[W]は。 | 40 | 80 | 100 | 120 | W = VI = I^2 · R W = 20^2 x 0.1 = 40 [W] Since this circuit has 3 wires, 3 x W = 3 x 40 = 120 [W] | 2011_1,
9 | Limit of time [minutes] during which a circuit breaker rated 20 [A] used in a low-voltage circuit must operate automatically when a current of 40 [A] continuously flows through it. (maximum time) is. |  | 1 | 2 | 3 | 4 | 2 | ['継続(けいぞく)- Continuation', '電流(でんりゅう)- Electric current', '定格(ていかく)- Rated value'] | {低圧}{電路}に{使用}する{定格}20[A]の{配線}用{遮断器}に40[A]の{電流}が{継続}して流れたとき、この{配線}用{遮断器}が{自動}的に動作しなければならない時間[分]の{限度}（最大の時間）は。 | 1 | 2 | 3 | 4 | The breaking time of a circuit breaker for wiring is stipulated to be within 60 minutes when the rated current is 1.25 times the rated current and within 2 minutes when the rated current is twice the rated current . In this case, 40A, which is double the 20A rating, is flowing, so it must be cut off within 2 minutes. Therefore, "2" is the correct answer. | 2011_1,
10 | In branch circuit design of low-voltage indoor wiring, what is inappropriate as a combination of the rated current of the circuit breaker for wiring and the outlet? |  | Picture_10_A | Picture_10_B | Picture_10_C | Picture_10_D | 3 | ['組合せ(くみあわせ)- Combination', '設計(せっけい)- Layout', '屋内配線(おくないはいせん)- Interior wiring'] | {低圧}{屋内配線}の{分岐}{回路}の{設計}で、配線用{遮断器}の{定格}{電流}と{コンセント}の{組合せ}として、{不適切}なものは。 | Picture_10_A | Picture_10_B | Picture_10_C | Picture_10_D | If the rated current of the circuit breaker for wiring is 30A, the outlet that can be used is 20A or more and 30A or less. | 2011_1,
11 | What is the most suitable outlet for an electric dishwasher used at home? |  | Outlets with ground terminals | Retaining outlets | Outlets with ground terminals and ground terminals | Hook-type outlets | 3 | ['接地(せっち)- Ground (electricity)', '電気(でんき)- Electricity'] | {住宅}で{使用}する{電気}食器洗い機用の{コンセント}として、最も適しているものは。 | {接地}{端子}付{コンセント} | 抜け止め形{コンセント} | {接地}{極}付{接地}{端子}付{コンセント} | 引掛形{コンセント} | Dishwashers are electrical appliances with a high risk of electric leakage because they are used in places where water is present. Regulations have made it obligatory to connect to an outlet with a grounding pole and to insulate it. | 2011_1,
12 | Equipment that is used in combination, and the combination is clearly incorrect. |  | Neon transformers and high-pressure mercury lamps | Zero-phase current transformers and earth leakage alarms | Photoelectric flashers and garden lights | Star-delta starters and low-voltage three-phase squirrel-cage induction motors for general use | 1 | ['漏電(ろうでん)- Short circuit', '変圧器(へんあつき)- Transformer', '機器(きき)- Equipment'] | {組み合わせ}て{使用}する{機器}で、その{組合せ}が明らかに誤っているものは。 | ネオン{変圧器}と{高圧}{水銀灯} | 零相{変流器}と{漏電}{警報器} | 光電式{自動}{点滅器}と庭園灯 | スターデルタ{始動}器と一般用{低圧}{三相}かご形{誘導電動機} | Neon transformers are preferred for use with neon discharge lamps. | 2011_1,
13 | What is the synchronous rotation speed [min-1] of a low-voltage three-phase squirrel-cage induction motor with a rated frequency of 60 [Hz] and four poles? |  | 1200 | 1500 | 1800 | 3000 | 3 | ['誘導電動機(ゆうどうでんどうき)- Induction motor', '周波数(しゅうはすう)- Frequency', '定格(ていかく)- Rated value'] | {定格}{周波数}60[Hz]、{極}数4の{低圧}{三相}かご形{誘導電動機}の{同期}{回転}{速度}[min-1]は。 | 1200 | 1500 | 1800 | 3000 | The rotation speed. (f = frequency p = number of poles) 120 x f/p = 120 x 60/4 = 1800 | 2011_1,
14 | What is the appropriate combination of the type of electrical work and the tools used in that work? |  | Metal pipe work and reamers | Synthetic resin pipe work and pipe benders | Metal wire work and clippers | Bus duct work and crimping pliers | 1 | ['圧着(あっちゃく)- Crimping', '工具(こうぐ)- Hand tool', '電気工事(でんきこうじ)- Electrical work'] | {電気}{工事}の{種類}と、その{工事}で{使用}する{工具}の{組合せ}として、{適切}なものは。 | {金属}{管}{工事}とリーマ | {合成}樹脂{管}{工事}とパイプベンダ | {金属}{線}ぴ{工事}とクリッパ | バスダクト{工事}と{圧着}ペンチ |  | 2011_1,
15 | What is the name of the instrument shown in the photo? | Picture_15 | Wiring circuit breaker | Earth leakage circuit breaker | Electromagnetic contactor | Earth leakage alarm | 2 | ['名称(めいしょう)- name; title', '写真(しゃしん)- Photo'] | {写真}に{示す}{器具}の{名称}は。 | {配線}用{遮断器} | {漏電}{遮断器} | {電磁}{接触}器 | {漏電}{警報器} |  | 2011_1,
16 | What are the uses of the material shown in the photo? | Picture_16 | Used to connect threadless conduits together. | Used to connect thin steel conduits. | Used to connect thick steel conduits. | Used to connect threadless conduits and metal outlet boxes. | 4 | ['材料(ざいりょう)- Materials'] | {写真}に{示す}{材料}の{用途}は。 | ねじなし{電線}{管}{相互}を{接続}するのに用いる。 | 薄鋼{電線}{管}{相互}を{接続}するのに用いる。 | 厚鋼{電線}{管}{相互}を{接続}するのに用いる。 | ねじなし{電線}{管}と{金属}製アウトレットボックスを{接続}するのに用いる。 |  | 2011_1,
17 | What is the purpose of the tool shown in the photo? |  | Used to strip the sheath and insulation coating of VVR cables. | Used to strip off the sheathing and insulating coating of the CV cable (for low voltage). | Used to strip the outer covering and insulation coating of the VVF cable. | Used to strip the insulating coating of VFF cords (vinyl flat cords). | 3 | ['絶縁(ぜつえん)- Insulation (electrical)', '外装(がいそう)- Packaging', '用途(ようと)- Use; purpose'] | {写真}に{示す}{工具}の{用途}は。 | VVRケーブルの{外装}や{絶縁}{被覆}をはぎ取るのに用いる。 | CVケーブル（{低圧}用）の{外装}や{絶縁}{被覆}をはぎ取るのに用いる。 | VVFケーブルの{外装}や{絶縁}{被覆}をはぎ取るのに用いる。 | VFFコード（ビニル平形コード）の{絶縁}{被覆}をはぎ取るのに用いる。 |  | 2011_1,
18 | What is the use of the equipment shown in the photo? |  | Used to adjust the brightness of incandescent lamps. | Used for automatic flashing when a person approaches. | Used to improve the power factor of fluorescent lamps. | Used to automatically flash street lights, etc. according to the brightness of the surroundings. | 4 | ['接近(せっきん)- Getting closer', '自動(じどう)- Automatic', '電灯(でんとう)- Electric light'] | {写真}に{示す}{器具}の{用途}は。 | 白熱{電灯}の明るさを調整するのに用いる。 | 人の{接近}による{自動}点滅に用いる。 | {蛍光灯}の{力率}改善に用いる。 | {周囲}の明るさに応じて街路灯などを{自動}点滅させるのに用いる。 |  | 2011_1,
19 | What is inappropriate as a synthetic resin pipe construction using hard vinyl chloride conduit? |  | Adhesive was used to connect the pipes to each other and the pipes to the box, so the insertion depth of the pipes was set to 0.5 times the outer diameter of the pipes. | Saddles were used for the straight part of the pipe, and the pipe was supported at intervals of 1[m]. | Moisture-proof devices were applied to the joints between pipes and boxes installed in humid locations. | With the three-phase 200[V] wiring, the metal pull box connected to the pipe installed in a place where people cannot easily touch it was grounded with class D grounding. | 1 | ['場所(ばしょ)- Place; location', '相互(そうご)- Reciprocal', '硬質(こうしつ)- Hardness'] | {硬質}塩化ビニル{電線}{管}による{合成}樹脂{管}{工事}として、{不適切}なものは。 | {管}{相互}及び{管}とボックスとの{接続}で、接着剤を{使用}したので{管}の差し込み深さを{管}の{外径}の0.5倍とした。 | {管}の直{線}{部分}はサドルを{使用}し、{管}を1[m]間隔で支持した。 | {湿気}の多い{場所}に{施設}した{管}とボックスとの{接続}{箇所}に、{防湿}装置を施した。 | {三相}200[V]{配線}で、人が{容易}に触れるおそれがない{場所}に{施設}した{管}と{接続}する{金属}製プルボックスに、D{種}{接地}{工事}を施した |  | 2011_1,
20 | What is unsuitable for single-phase 3-wire 100/200V indoor wiring work in humid open areas? |  | Synthetic resin pipe work | Metal duct work | Metal pipe work | Cable work | 2 | ['金属(きんぞく)- Metal', '湿気(しっけ)- Moisture'] | {湿気}の多い展開した{場所}の{単相}3線式100/200V{屋内配線}{工事}として、{不適切}なものは。 | {合成}樹脂{管}{工事} | {金属}ダクト{工事} | {金属}{管}{工事} | ケーブル{工事} |  | 2011_1,
21 | What is inappropriate as a method of indoor wiring work to install a room air conditioner with a three-phase 200 [V] and rated power consumption of 2.8 [kW] in a house with a store? |  | Install electric wires so that they cannot be easily touched by people. | Install a dedicated wiring circuit breaker in the electric circuit. | Install an earth leakage circuit breaker in the electric circuit. | Connect the room air conditioner with indoor wiring and an outlet. | 4 | ['専用(せんよう)- Dedicated use', '電路(でんろ)- Electrical circuit', '三相(さんそう)- Three phases'] | {店舗}付き{住宅}に{三相}200[V]、{定格}消費{電力}2.8[kW]のルームエアコンを{施設}する{屋内配線}{工事}の{方法}として、{不適切}なものは。 | {電線}は人が{容易}に触れるおそれがないように{施設}する。 | {電路}には{専用}の{配線}用{遮断器}を{施設}する。 | {電路}には{漏電}{遮断器}を{施設}する。 | ルームエアコンは{屋内配線}と{コンセント}で{接続}する。 |  | 2011_1,
22 | What is inappropriate for use at the terminal A or B part of metal pipe construction installed outside the rain line shown in the figure? |  | An entrance cap was used in part A. | A terminal cap was used. | The entrance cap was used in the B part. | A terminal cap was used for the B part. | 2 | ['不適切(ふてきせつ)- Unsuitable', '部分(ぶぶん)- Portion', '末端(まったん)- Terminal'] | {図}に{示す}雨{線}外に{施設}する{金属}{管}{工事}の{末端}A又はB{部分}に{使用}するものとして、{不適切}なものは。 | A{部分}にエン{トランス}キャップを{使用}した。 | A{部分}にターミナルキャップを{使用}した。 | B{部分}にエン{トランス}キャップを{使用}した。 | B{部分}にターミナルキャップを{使用}した。 |  | 2011_1,
23 | What is inappropriate for neon discharge lamp construction where the indoor tube lamp circuit uses more than 1000 [V]? However, it shall be installed in a place where there is no risk of human beings touching it easily. |  | The 100[V] power supply circuit to the neon transformer was a dedicated circuit, and a 20[A] circuit breaker was installed. | The wiring on the secondary side (tube lamp circuit) of the neon transformer was installed in a concealed place where it could not be inspected. | D class grounding work was applied to the metal outer box of the neon transformer. | Neon wires were used for the wiring on the secondary side (tube lamp circuit) of the neon transformer. | 2 | ['配線(はいせん)- Wiring', '変圧器(へんあつき)- Transformer', '放電灯(ほうでんとう) - Arc lamp', '屋内(おくない)- Indoor'] | {屋内}の{管}灯{回路}の{使用}{回路}が1000[V]を超えるネオン放{電灯}の{工事}として、{不適切}なものは。 ただし、人が{容易}に触れるおそれがない{場所}に{施設}するものとする。 | ネオン{変圧器}への100[V]{電源}{回路}は、{専用}{回路}とし、20[A]{配線}用{遮断器}を{設置}した。 | ネオン{変圧器}の二次側（{管}灯{回路}）の{配線}を、{点検}できない隠ぺい{場所}に{施設}した。 | ネオン{変圧器}の{金属}製{外箱}にD{種}{接地}{工事}を施した。 | ネオン{変圧器}の二次側（{管}灯{回路}）の{配線}を、ネオン{電線}を{使用}し、がいし引き{工事}により{施設}し、{電線}の支持点間の{距離}を1[m]とした。 |  | 2011_1,
24 | What is the purpose of using a neon voltage detector? |  | Measure the illuminance of the neon discharge lamp. | Check the continuity of the neon tube lamp circuit. | Check if the electric circuit is charged. | Measure the leakage current of the circuit. | 3 | ['導通(どうつう)- Conduction', '照度(しょうど)- Illuminance', '検電器(けんでんき)- Voltage detector'] | ネオン式{検電器}を{使用}する{目的}は。 | ネオン放{電灯}の{照度}を{測定}する。 | ネオン{管}灯{回路}の{導通}を調べる。 | {電路}の{充電}の有無を{確認}する。 | {電路}の漏れ{電流}を{測定}する。 |  | 2011_1,
25 | There was a symbol like the figure on the dial of an electric meter. What is the correct meaning of the symbol? |  | Inductive type with scale plate placed horizontally. | Use a rectifier with the scale plate set vertically. | Use a movable iron piece with the scale plate set vertically. | Use the movable iron plate with the scale plate placed horizontally. | 3 | ['計器(けいき)- Meter', '電気(でんき)- Electricity'] | {電気}{計器}の目盛板に{図}のような{記号}があった。{記号}の意味として、{正しい}ものは。 | {誘導}形で目盛板を{水平}に置いて{使用}する。 | 整流形で目盛板を鉛直に立てて{使用}する。 | {可動}鉄片形で目盛板を鉛直に立てて{使用}する。 | {可動}鉄片形で目盛板を{水平}に置いて{使用}する。 |  | 2011_1,
26 | The following table shows the working voltage of a low-voltage circuit separated by a switch or overcurrent circuit breaker in a place where electricity is used, and the minimum value of insulation resistance between wires and between the circuit and the ground. What is the correct combination of numbers that fit in the blanks of A, B, and C? |  | A 0.1、B 0.2、C 0.4 | A 0.1、B 0.3、C 0.5 | A 0.2、B 0.3、C 0.4 | A 0.2、B 0.4、C 0.6 | 1 | ['大地(だいち)- Ground; earth', '数値(すうち)- Numerical value'] | 次表は、{電気}{使用}{場所}の{開閉器}又は過{電流}{遮断器}で区切られる{低圧}{電路}の{使用}{電圧}と{電線}{相互}間及び{電路}と{大地}との間の{絶縁}抵抗の{最小}値についての表である。 A・B・Cの空欄にあてはまる{数値}の{組合せ}として、{正しい}ものは。 | A 0.1、B 0.2、C 0.4 | A 0.1、B 0.3、C 0.5 | A 0.2、B 0.3、C 0.4 | A 0.2、B 0.4、C 0.6 |  | 2011_1,
27 | Anything that cannot be measured by a commonly used circuit meter (tester). |  | AC voltage | Circuit resistance | Leakage current | DC voltage | 3 | ['測定(そくてい)- Measurement', '回路計(かいろけい)- Multimeter'] | 一般に{使用}される{回路}計（テスタ）によって{測定}できないものは。 | {交流}{電圧} | {回路}抵抗 | 漏れ{電流} | {直流}{電圧} |  | 2011_1,
28 | Under the Electrician Law, what kind of work cannot be done even by a person who has received a second-class electrician's license? |  | Grounding work for general-use electric facilities | Neon work for general-use electric facilities | Construction of emergency stand by power generators for private electric facilities (demand equipment of less than 500 [kW]) | Private electric facilities Installation work of pipes for underground electric wires (demand facilities of less than 500 [kW]) | 3 | ['家用(かよう)- Domestic uses', '電気工(でんきこう)- Electrician', '免状(めんじょう)- Licence'] | {電気}{工事}士法において、第二{種}{電気}{工事}士{免状}の交付を受けている者であってもできない{工事}は。 | 一般用{電気}工{作物}の{接地}{工事} | 一般用{電気}工{作物}のネオン{工事} | 自{家用}{電気}工{作物}（500[kW]未満の{需要}{設備}）の非常用予備{発電}装置の{工事} | 自{家用}{電気}工{作物}（500[kW]未満の{需要}{設備}）の{地中}{電線}用の{管}の{設置}{工事} |  | 2011_1,
29 | Except for special cases, what is the maximum voltage to ground [V] that can be used for indoor electric circuits in a house? |  | 100 | 150 | 200 | 250 | 2 | ['電路(でんろ)- Electrical circuit', '住宅(じゅうたく)- Residential building'] | 特別な{場合}を除き、{住宅}の{屋内}{電路}に{使用}できる{対地}{電圧}の{最大値}[V]は。 | 100 | 150 | 200 | 250 |  | 2011_1,
30 | What is subject to the application of electric tools for general use. However, all of them shall be installed in one premises. |  | A kindergarten equipped with a solar cell power generation facility with a low-voltage power supply of 40 [kW] and an output of 15 [kW] | A machine factory with a high-voltage power supply of 65 [kW] | A low-voltage power supply, the power received A movie theater equipped with an emergency internal combustion power generation facility with an output of 35 [kW] and an output of 15 [kW] | A convenience store with a high-voltage receiving power of 40 [kW] | 1 | ['低圧(ていあつ)- Low voltage', '電力(でんりょく)- Electric power', '構内(こうない)- Premises; grounds', '需要(じゅよう)- Demand'] | 一般用{電気}工{作物}の{適用}を受けるものは。ただし、いずれも1{構内}に{設置}するものとする。 | {低圧}{受電}で、{受電}{電力}40[kW]、{出力}15[kW]の太陽{電池}{発電}{設備}を備えた幼稚園 | {高圧}{受電}で、{受電}{電力}65[kW]の{機械}{工場} | {低圧}{受電}で、{受電}{電力}35[kW]、{出力}15[kW]の非常用内燃力{発電}{設備}を備えた{映画館} | {高圧}{受電}で、{受電}{電力}40[kW]のコンビニエンスストア |  | 2011_1,
31 | What is the maximum voltage [V] that can be used in the small force circuit shown in ①? |  | 24 | 30 | 48 | 60 | 4 | ['最大値(さいだいち)- Maximum', '電圧(でんあつ)- Voltage', '回路(かいろ)- Circuit', '部分(ぶぶん)- Portion'] | ①で{示す}{部分}の小{勢力}{回路}で{使用}できる{電圧} の{最大値} [V] は。 | 24 | 30 | 48 | 60 |  | 2011_1,
32 | The name of the low-voltage cable indicated by ② is |  | 600V Vinyl Insulated Vinyl Sheath Cable Round | 600V cross-linked polyethylene insulated vinyl sheath cable | 600V rubber insulated chloroprene sheath cable | 600V polyethylene insulated vinyl sheath cable | 2 | ['絶縁(ぜつえん)- Insulation', '円形(えんけい)- Round shape', '低圧(ていあつ)- Low voltage'] | ②で{示す}{低圧}ケーブルの{名称}は | 600V ビニル{絶縁}ビニルシースケーブル丸形 | 600V {架橋}ポリエチレン{絶縁}ビニルシースケーブル | 600V ゴム{絶縁}クロロプレンシースケーブル | 600V ポリエチレン{絶縁}ビニルシースケーブル |  | 2011_1,
33 | What is the maximum allowable value [Ω] for the grounding resistance of the grounding electrode of the outlet indicated by ③? |  | 10 | 100 | 300 | 500 | 4 | ['抵抗(ていこう)- Resistance', '接地(せっち)- Ground (electricity)'] | ③で{示す}{コンセント}の{接地}{極}の{接地}抵抗とし て, {許容}される{最大値} [Ω] は. | 10 | 100 | 300 | 500 |  | 2011_1,
34 | What is the maximum value [A] of the rated current of the circuit breaker for wiring leading to the Western-style outlet shown in ④? |  | 15 | 20 | 30 | 40 | 4 | ['電流(でんりゅう)- Electric current', '遮断器(しゃだんき)- Circuit breaker', '洋室(ようしつ)- Western-style room'] | ④で{示す}{洋室}の{コンセント}へ至る{配線}用{遮断} 器の{定格}{電流}の{最大値} [A] は。 | 15 | 20 | 30 | 40 |  | 2011_1,
35 | What is the purpose of using the equipment with the symbol shown in ⑤? |  | Cut off the unbalanced current. | Cuts off only the ground fault current. | Cut off only the short-circuit current. | Cut off overcurrent and ground fault current. | 4 | ['電流(でんりゅう)- Electric current', '目的(もくてき)- Purpose', '記号(きごう)- Symbol'] | ⑤で{示す}{図}{記号}の{器具}を用いる{目的}は。 | {不平衡}{電流}を{遮断}する。 | 地絡{電流}のみを{遮断}する。 | 短絡{電流}のみを{遮断}する。 | 過{電流}と地絡{電流}を{遮断}する。 |  | 2011_1,
36 | What is the meaning of "WP", which is a side note of the symbol shown in ⑥? |  | Wide type | Outdoor type | Rainproof type | Drip-proof type | 3 | ['表示(ひょうじ)- Indication', '記号(きごう)- Symbol'] | ⑥で{示す}{図}{記号}の傍記{表示} 「WP」 の意味は。 | ワイド形 | {屋外}形 | 防雨形 | 防滴形 |  | 2011_1,
37 | I would like to install a chandelier as a lighting fixture in the part indicated by ⑦. The symbol is |  | Picture_37_A | Picture_37_B | Picture_37_C | Picture_37_D | 1 | ['記号(きごう)- Symbol', '部分(ぶぶん)- Portion'] | ⑦で{示す}{部分}に照明{器具}としてシャンデリヤ を取り付けたい。 {図}{記号}は。 | Picture_37_A | Picture_37_B | Picture_37_C | Picture_37_D |  | 2011_1,
38 | I want to install an outlet with a ground terminal in the part indicated by ⑧. The symbol is |  | Picture_38_A | Picture_38_B | Picture_38_C | Picture_38_D | 4 | ['接地(せっち)- Ground (electricity)'] | ⑧で{示す}{部分}に{接地}{端子}付{コンセント}を取り 付けたい。 {図}{記号}は。 | Picture_38_A | Picture_38_B | Picture_38_C | Picture_38_D |  | 2011_1,
39 | Attach the incandescent lamp to the part indicated by ⑨ with a cord. What is the correct combination of code and minimum cross-sectional area that can be used? |  | Vinyl cord 1.25 (mm²) | Round rubber cord 0.75mm² | Vinyl rubber cord 0.75 [mm] | Bagged rubber cord 0.5mm² | 2 | ['断面積(だんめんせき)- Cross-sectional area', '最小(さいしょう)- Smallest', '白熱電球(はくねつでんきゅう)- Light bulb'] | ⑨で{示す}{部分}にコード吊りで{白熱電球}を取り 付ける。{使用}できるコードと{最小}{断面積}の {組合せ}として、{正しい}ものは。 | ビニルコード 1.25 (mm²) | 75mm²) | ビニルキャブタイヤコード 0.75 [mm] | 袋打ちゴムコード 0.5mm²) |  | 2011_1,
40 | What is the minimum number of wires (number of cores) of the part indicated by 10? |  | 3 | 4 | 5 | 6 | 3 | ['最少(さいしょう)- fewest'] | ⑩で{示す}{部分}の{最少}{電線}{本数} (心線数) は。 | 3 | 4 | 5 | 6 |  | 2011_1,
41 | What tools are used for the construction of the part indicated by ⑪? |  | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D | 1 | ['使用(しよう)- Use'] | ⑪で{示す}{部分}の{工事}に使 用する{工具}は。 | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D |  | 2011_1,
42 | Equipment with the symbol ⑫shown in . |  | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D | 3 | ['器具(きぐ)- Utensil'] | ⑫で{示す}{図}{記号}の{器具}は。 | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D |  | 2011_1,
43 | As for the equipment with the symbol shown in ⑬. However, the diagram below the photo shows the configuration of the contacts. |  | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D | 3 | ['接点(せってん)- Tangent point', '構成(こうせい)- Composition'] | ⑬で{示す}{図}{記号}の{器具}は。 ただし、{写真}下の{図}は、 {接点}の{構成}を{示す}。 | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D |  | 2011_1,
44 | ⑭ What is the equipment with the graphical symbol? |  | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D | 3 | ['接点(せってん)- Tangent point', '構成(こうせい)- Composition'] | ⑭で{示す}{図}{記号}の{器具}は。 | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D |  | 2011_1,
45 | As for the equipment with the symbol shown in ⑮. |  | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D | 1 | ['記号(きごう)- Symbol'] | ⑮で{示す}{図}{記号}の{器具}は。 | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D |  | 2011_1,
46 | The plate attached to the part indicated by ⑯ is |  | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D | 2 | ['部分(ぶぶん)- Portion'] | ⑯で{示す}{部分}に取り付け. るプレートは | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D |  | 2011_1,
47 | What is the equipment to be attached to the part indicated by ⑰? |  | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D | 2 | ['器具(きぐ)- Utensil'] | ⑰で{示す}{部分}に取り付ける{器具}は。 | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D |  | 2011_1,
48 | Negative current flowing to the part indicated by ⑱. for measuring the load current. |  | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D | 4 | ['電流(でんりゅう)- Electric current', '部分(ぶぶん)- Portion'] | ⑱で{示す}{部分}に{流れる}負 。 荷の{電流}を{測定}するため のものは。 | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D |  | 2011_1,
49 | Inside the ceiling of the part indicated by ⑲. What is the appropriate combination of the type and minimum number of ring sleeves to be used when all connections in the joint box are crimp connections? |  | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D | 1 | ['最少(さいしょう)- Fewest', '種類(しゅるい)- Variety', '圧着(あっちゃく)- Crimping', '接続(せつぞく)- Connection'] | ⑲で{示す}{部分}の{天井}内の。ジョイントボックス内において、{接続}をすべて{圧着}{接続}とする{場合}、{使用}するリングスリーブの{種類}と{最少}{個数}の{組合せ}で、{適切}なものは。 | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D |  | 2011_1,
50 | What is the appropriate tool for the construction of the joint box for VVF shown in ⑳ by crimping connection with ring sleeve E type? |  | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D | 3 | ['工具(こうぐ)- Hand tool', '圧着(あっちゃく)- Crimping', '工事(こうじ) - Construction work'] | ⑳で{示す} VVF 用ジョイントボックス{部分}の{工事}を、 リングスリーブ E形による{圧着}{接続}で行う{場合}に用いる{工具}として、{適切}なものは | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D |  | 2011_1,