## Sheet1
no | Eng | Picture | Option_1_Eng | Option_2_Eng | Option_3_Eng | Option_4_Eng | Ans | Vocab | Jpn | Option_1_Jpn | Option_2_Jpn | Option_3_Jpn | Option_4_Jpn | Exp | comment
1 | Assuming that the diameter of the conductor of a vinyl insulated wire (single core) is D and the length is L, what is an incorrect statement regarding the resistance and allowable current of this wire? |  | The wire resistance is proportional to L. | The resistance of a wire is inversely proportional to the square of D. | The allowable current increases as the ambient temperature rises. | The allowable current increases as D increases. | 3 | ['電流(でんりゅう)- Electric current', '直径(ちょっけい)- Diameter', '導体(どうたい)- Conductor (electricity)', '絶縁(ぜつえん)- Insulation (electrical )'] | ビニル{絶縁}{電線}（単心）の{導体}の{直径}をD、{長さ}をLとするとき、この{電線}の抵抗と{許容}{電流}に関する{記述}として、誤っているものは。 | {電線}の抵抗は、Lに比例する。 | {電線}の抵抗は、Dの2乗に反比例する。 | {許容}{電流}は、{周囲}の{温度}が上昇すると、大きくなる。 | {許容}{電流}は、Dが大きくなると、大きくなる。 |  | 2011_2,
2 | In the AC circuit shown in the figure, the voltage V[V] across reactance 8[Ω] is: | Picture_2 | 43 | 57 | 60 | 80 | 4 |  | {図}のような{交流}{回路}で、リアクタンス8[Ω]の{両端}の{電圧}V[V]は。 | 43 | 57 | 60 | 80 | Z [Ω] = √ (resistance R^2 + reactance X^2) Z [Ω] = √6^2 + 8^2 = 10[Ω] I[A]=100[V]/10[Ω]=10[A] E[V]=10[A]*8[Ω]=80[V] | 2011_2,
3 | When a load with a power consumption of 2.0 [kW] and a power factor of 80 [%] is connected to a single-phase 200 [V] circuit, what is the current [A] that flows through the circuit? |  | 5.8 | 8.0 | 10.0 | 12.5 | 4 | ['電流(でんりゅう)- ', '場合(ばあい)- Case; Situation', '力率(りきりつ)- Power factor', '回路(かいろ)- Circuit'] | {単相}200[V]の{回路}に、消費{電力}2.0[kW]、{力率}80[%]の{負荷}を{接続}した{場合}、{回路}に{流れる}{電流}[A]は。 | 5.8 | 8.0 | 10.0 | 12.5 | I = P/V×cosθ, I = 2.0×1000/200×0.8 = 12.5. | 2011_2,
4 | As shown in the figure, a capacitor C was installed for a load with a lagging power factor to improve the power factor to 100[%]. The voltage V across the load at this time is where r is the wire resistance. | Picture_4 | Higher than before the capacitor was installed. | Lower than before the capacitor was installed. | There is no change compared to before the capacitor was installed. | Becomes zero. | 1 | ['電圧(でんあつ)- Voltage', '設置(せっち)- establishment; institution', '負荷(ふか)- Load'] | {図}のように、遅れ{力率}の{負荷}に対してコンデンサCを{設置}して、{力率}を100[%]に改善した。このときの{負荷}{両端}の{電圧}Vは。 ただし、rは{電線}の抵抗である。 | コンデンサ{設置}前と比べて高くなる。 | コンデンサ{設置}前と比べて低くなる。 | コンデンサ{設置}前と比べて変化しない。 | 零になる。 |  | 2011_2,
5 | When a three-phase AC voltage is applied to a three-phase load as shown in the figure, a current of 15[A] flows in each line. Line voltage E[V] is |  | 120 | 169 | 208 | 240 | 3 | ['電圧(でんあつ)- Low Voltage', '電流(でんりゅう)- Electric current'] | {図}のような{三相}{負荷}に{三相}{交流}{電圧}を加えたとき、各{線}に15[A]の{電流}が流れた。{線}間{電圧}E[V]は。 | 120 | 169 | 208 | 240 | E (line voltage) = √3 x load phase voltage E = 1.73 x 120 = 207.6 (≈ 208) | 2011_2,
6 | In low-voltage indoor wiring work using metal pipes, if five 2.0 [mm] 600V vinyl insulated wires (annealed copper wires) are installed inside the pipe, what is the allowable current [A] per wire? However, the ambient temperature should be 30[°C] or less, and the current reduction factor should be 0.56. |  | 10 | 15 | 19 | 27 | 3 | ['電流(でんりゅう)- Electric current', '周囲温度(しゅういおんど)- Ambient temperature', '許容(きょよう)- Permission', '絶縁(ぜつえん)- Insulation ', '低圧(ていあつ)- Low Voltage'] | {金属}管による{低圧}{屋内配線}{工事}で、{管内}に2.0[mm]の600Vビニル{絶縁}{電線}（軟{銅線}）5本を収めて{施設}した{場合}、{電線}1本{当たり}の{許容}{電流}[A]は。 ただし、{周囲}{温度}は30[℃]{以下}、{電流}{減少}{係数}は0.56とする。 | 10 | 15 | 19 | 27 | 2.0mm diameter allowable current is 35A So, 35×0.56=19.6A | 2011_2,
7 | In a single-phase three-wire circuit as shown in the figure, when the resistance of each wire is 0.1 [Ω] and the current flowing through the load is 10 [A], the power loss [W] in this wire line is: However, the load shall be a resistive load. | Picture_7 | 30 | 80 | 120 | 160 | 2 | ['抵抗(ていこう)- Resistance', '電流(でんりゅう)- Electric current', '回路(かいろ)- Circuit'] | {図}のような{単相}3線式{回路}で、{電線}1線{当たり}の抵抗が0.1[Ω]、{負荷}に{流れる}{電流}がいずれも10[A]のとき、この{電線}路の{電力}損失[W]は。 ただし、{負荷}は抵抗{負荷}とする。 | 30 | 80 | 120 | 160 | 20[A]*0.1[Ω]=2[V] . 2[V]*20[A]=40[W] Since there are two of these, 40*2=80[W]. | 2011_2,
8 | In a 3-phase 3-wire circuit as shown in the figure, when the resistance per wire is r [Ω] and the wire current is I [A], what is the formula for the voltage drop (V1-V2) [V]? |  | √3I^2r | √3Ir | 2Ir | 2√3Ir | 2 | ['電圧降下(でんあつこうか)- Voltage drop', '回路(かいろ)- Circuit', '三相(さんそう)- Three phases'] | {図}のような{三相}3線式{回路}で、{電線}1線{当たり}の抵抗がr[Ω]、線{電流}がI[A]であるとき、{電圧}降下(V1-V2)[V]を{示す}式は。 | √3I^2r | √3Ir | 2Ir | 2√3Ir | The voltage drop formula. (V₁ーV₂)=√3×r×l | 2011_2,
9 | As shown in the figure, when a three-phase motor and a three-phase electric heater are connected to a low-voltage indoor main line, what is the minimum current value [A] that determines the thickness of the main line? However, the demand rate is assumed to be 100[%]. |  | 90 | 96 | 105 | 112 | 2 | ['太い(ふと)- Fat; thick', '幹線(かんせん)- Main line', '電動機(でんどうき)- Electric motor'] | {図}のように、{三相}{電動機}と{三相}{電熱器}が{低圧}{屋内}{幹線}に{接続}されている{場合}、{幹線}の太さを決める{根拠}となる{電流}の{最小}{値}[A]は。 ただし、{需要}率は100[%]とする。 | 90 | 96 | 105 | 112 | I( M )=30+30=60A I(H)=15+15=30A I≧1.1×I(M)+I(H))×Demand rate [%]÷100 Therefore, I≧(1.1×60+30)×100÷100 = 96 | 2011_2,
10 | What is the appropriate combination of the diameter of the wire (annealed copper wire) of the branch circuit protected by the circuit breaker with a rated current of 30[A] and the symbol of the outlet that can be connected? However, the current reduction factor shall be ignored. |  | Picture_10_A | Picture_10_B | Picture_10_C | Picture_10_D | 1 | ['減少(げんしょう)- Decrease', '係数(けいすう)- Coefficient', '記号(きごう)- Symbol; sign', '回路(かいろ)- Circuit', '定格(ていかく)- Rated value'] | {定格}{電流}30[A]の{配線}用{遮断器}で保護される{分岐}{回路}の{電線}（軟{銅線}）の太さと、{接続}できる{コンセント}の{記号}の{組合せ}として、{適切}なものは。 ただし、{電流}{減少}{係数}は無視するものとする。 | Picture_10_A | Picture_10_B | Picture_10_C | Picture_10_D |  | 2011_2,
11 | What is the purpose of the ring reducer used in metal pipe work? |  | Both are used to connect metal pipes that cannot be turned. | Used when connecting metal pipes at right angles. | Attached to the end of a metal pipe and used to protect the coating of the wire that is drawn out. | Used when the diameter of the knockout (punched hole) of the outlet box is larger than the outer diameter of the metal tube connected to it. | 4 | ['接続(せつぞく)- Connection', '分岐(ぶんき)- Divergence', '電流(でんりゅう)- Electric current'] | {金属}{管}{工事}において{使用}されるリングレジューサの{使用}{目的}は。 | 両方とも回すことのできない{金属}{管}{相互}を{接続}するときに{使用}する。 | {金属}{管}{相互}を{直角}に{接続}するときに{使用}する。 | {金属}{管}の{管}端に取り付け、引き出す{電線}の{被覆}を保護するときに{使用}する。 | アウトレットボックスのノックアウト（打ち抜き穴）の径が、それに{接続}する{金属}{管}の{外径}より大きいときに{使用}する。 |  | 2011_2,
12 | What is the wrong combination of electrical work and the tools used for that work? |  | Drilling holes in metal cabinets and knockout puncher | Cutting thin steel conduits and plica knife | Drilling holes in wooden ceiling boards for conduits and cutting blades | Cutting electric wires, messenger wires, etc. Work to remove slack and wire tensioner | 2 | ['工具(こうぐ)- Hand tool', '羽(はね)- Feather; plume; down', '作業(さぎょう)- work; operation; task'] | {電気}{工事}の{作業}と、その{作業}で{使用}する{工具}の{組合せ}として誤っているものは。 | {金属}製キャビネットに穴をあける{作業}とノックアウトパンチャ | 薄鋼{電線}{管}を{切断}する{作業}とプリカナイフ | {木造}{天井}板に{電線}{管}を通す穴をあける{作業}と羽根ぎり | {電線}、メッセンジャワイヤ等のたるみを取る{作業}と張線器 |  | 2011_2,
13 | What electric wires can be used when installing low-voltage underground electric wires by direct burial? |  | Outdoor vinyl insulated wire (OW) | 600V cross-linked polyethylene insulated vinyl sheathed cable (CV) | Vinyl insulated lead-in wire (DV) | 600V vinyl insulated wire (IV) | 2 | ['絶縁(ぜつえん)- Insulation', '電線(でんせん)- Cable', '線路(せんろ)- Railway track'] | {低圧}の{地中}{電線}路を{直接}埋設式により{施設}する{場合}に、{使用}できる{電線}は。 | {屋外}用ビニル{絶縁}{電線}(OW) | 600V{架橋}ポリエチレン{絶縁}ビニルシースケーブル(CV) | 引込用ビニル{絶縁}{電線}(DV) | 600Vビニル{絶縁}{電線}(IV) |  | 2011_2,
14 | What is the purpose of using ballasts for mercury lamps? |  | Stabilize the discharge. | Improve power factor. | Prevent noise (radio interference). | Increase luminous flux | 1 | ['放電(ほうでん)- Electrostatic discharge', '安定器(あんていき)- Stabilizer'] | {水銀灯}に用いる安定器の{使用}{目的}は。 | 放電を安定させる。 | {力率}を改善する。 | 雑音（電波{障害}）を防止する。 | 光束を増やす。 |  | 2011_2,
| What is the purpose of the tool shown in the photo? | Picture_15 | Used for chamfering cut ends of metal pipes. | Used for drilling wooden poles. | Used for drilling holes in iron plates and various alloy plates. | Used for drilling holes in concrete walls. | 3 | ['各種(かくしゅ)- Every kind; all sorts', '用途(ようと)- Use; service', '写真(しゃしん)- Photography'] | {写真}に{示す}{工具}の{用途}は。 | {金属}{管}切り口の{面取り}に{使用}する。 | 木柱の{穴あけ}に{使用}する。 | {鉄板}、各{種}合金板の{穴あけ}に{使用}する。 | コンクリート{壁}の{穴あけ}に{使用}する。 |  | 2011_2,
| What is the name of the material shown in the photo? | Picture_16 | Synthetic resin wire | Hard vinyl chloride conduit | Synthetic resin flexible conduit | Metal flexible conduit | 4 | ['硬質(こうしつ)- Hardness', '材料(ざいりょう)- Materials; ingredients'] | {写真}に{示す}{材料}の{名称}は。 | {合成}樹脂{線}ぴ | {硬質}塩化ビニル{電線}{管} | {合成}樹脂製可とう{電線}{管} | {金属}製可とう{電線}{管} |  | 2011_2,
17 | What is the name of the instrument shown in the photo? | Picture_17 | Key socket | Lamp receptacle | Pull socket | Waterproof socket with wire | 4 | ['名称(めいしょう)- Name; title', '器具(きぐ)- Tool; instrument'] | {写真}に{示す}{器具}の{名称}は。 | キーソケット | ランプレセプタクル | プルソケット | {線}付防水ソケット |  | 2011_2,
18 | What is the name of the instrument shown in the photo? | Picture_18 | Time switch | Dimmer | Watt meter | Auto flasher | 1 | ['自動(じどう)- Automatic', '調光器(ちょうこうき)- Dimmer control'] | {写真}に{示す}{器具}の{名称}は。 | タイム{スイッチ} | {調光器} | {電力}量計 | {自動}{点滅器} |  | 2011_2,
19 | What is inappropriate for connecting insulated wires in single-phase 100[V] indoor wiring work? |  | Sufficiently covered with insulation that is equal to or greater than the insulation of the insulated wire. | The tensile strength of the wire decreased by 15[%]. | A ring sleeve E type was used to crimp the ends. | The electrical resistance of the wire has increased by 10[%]. | 4 | ['電線(でんせん)- Electric cable', '絶縁(ぜつえん)- Insulation', '単相(たんそう)- Single phase'] | {単相}100[V]の{屋内配線}{工事}における{絶縁}{電線}{相互}の{接続}で、{不適切}なものは。 | {絶縁}{電線}の{絶縁}物と同等以上の{絶縁}{効力}のあるもので十分{被覆}した。 | {電線}の引張{強さ}が15[%]{減少}した。 | {終端部}を{圧着}{接続}するのにリングスリーブE形を{使用}した。 | {電線}の{電気}抵抗が10[%]{増加}した。 |  | 2011_2,
20 | For items that cannot omit Class D grounding work. However, it is assumed that the circuit is equipped with an earth leakage breaker with a rated sensitivity current of 30[mA] and an operation time of 0.1[second]. |  | A 4[m] long metal pipe containing three-phase 200[V] power wiring installed in a dry place. | Metal enclosure of a three-phase 200[V] room air conditioner installed on a dry concrete floor. | A three-phase 200[V] induction motor pedestal installed to handle on a dry wood floor. | 8[m] long metal tube containing single-phase 3-wire 100/200V wiring installed in a dry location. | 2 | ['場所(ばしょ)- Place; location', '動力(どうりょく)- Power transmission', '感度(かんど)- Sensitivity'] | D{種}{接地}{工事}を{省略}できないものは。 ただし、{電路}には{定格}{感度}{電流}30[mA]、{動作時間}0.1[秒]の{漏電}{遮断器}が取り付けられているものとする。 | 乾燥した{場所}に{施設}する{三相}200[V]動力{配線}を収めた{長さ}4[m]の{金属}{管}。 | 乾燥したコンクリートの{床}に{施設}する{三相}200[V]のルームエアコンの{金属}製{外箱}{部分}。 | 乾燥した木製の{床}の上で取り扱うように{施設}する{三相}200[V]{誘導電動機}の鉄台。 | 乾燥した{場所}に{施設}する{単相}3線式100/200V{配線}を収めた{長さ}8[m]の{金属}{管}。 |  | 2011_2,
21 | What is the appropriate type of construction work depending on the facility location for indoor wiring with a working voltage of 100 [V]? |  | Metal wire construction in a dry place that cannot be inspected | Lighting duct construction in a dry place with a concealed place that can be inspected | Construction of metal ducts in humid areas where inspection is hidden | Flat protective layer construction in humid areas where inspection can be concealed | 2 | ['金属(きんぞく)- Metal', '種類(しゅるい)- Variety', '施設(しせつ)- Home ', '電圧(でんあつ)- Voltage'] | {使用}{電圧}100[V]の{屋内配線}の{施設}{場所}による{工事}の{種類}として、{適切}なものは。 | {点検}できない隠ぺい{場所}であって、乾燥した{場所}の{金属}{線}ぴ{工事} | {点検}できる隠ぺい{場所}であって、乾燥した{場所}のライティングダクト{工事} | {点検}できる隠ぺい{場所}であって、{湿気}の多い{場所}の{金属}ダクト{工事} | {点検}できる隠ぺい{場所}であって、{湿気}の多い{場所}の平形保護層{工事} |  | 2011_2,
22 | Single-phase three-wire 100/200[V] indoor wiring work that cannot omit earth leakage breakers. |  | Construction of lighting ducts installed in places where people may easily touch | Wiring work for small power circuits | Work to supply electricity to lighting fixtures attached to the ceiling in a dry place | Work to supply electricity to a motor with a working voltage of 200[V] that has a metal outer case installed in a dry place. | 1 | ['金属製(きんぞくせい)_ Made of metal', '電気(でんき)- Electricity', '工事(こうじ)- Construction work', '屋内配線(おくないはいせん)- Interior wiring'] | {単相}3線式100/200[V]の{屋内配線}{工事}で{漏電}{遮断器}を{省略}できないものは。 | 人が{容易}に触れるおそれのある{場所}に{施設}するライティングダクト{工事} | 小{勢力}{回路}の{配線}{工事} | 乾燥した{場所}の{天井}に取り付ける照明{器具}に{電気}を供給する{工事} | 乾燥した{場所}に{施設}した、{金属}製{外箱}を有する{使用}{電圧}200[V]の{電動機}に{電気}を供給する{工事} |  | 2011_2,
23 | What is described in the "Interpretation of Technical Standards for Electrical Equipment" as a construction method for low-voltage indoor wiring by cable construction when the cable is close to the gas pipe? |  | Be installed so as not to come into contact with gas pipes. | May come in contact with gas pipes. | Keep a distance of 10[cm] or more from the gas pipe. | Keep a distance of 30[cm] or more from the gas pipe. | 1 | ['距離(きょり)- Distance', '接触(せっしょく)- Touch', '電気設備(でんきせつび)- Electrical equipment', '工事(こうじ)- construction work'] | ケーブル{工事}による{低圧}{屋内配線}で、ケーブルがガス{管}と{接近}する{場合}の{工事}{方法}として、「{電気}{設備}の{技術基準}の{解釈}」にはどのように{記述}されているか。 | ガス{管}と{接触}しないように{施設}すること。 | ガス{管}と{接触}してもよい。 | ガス{管}との{離隔}{距離}を10[cm]以上とすること。 | ガス{管}との{離隔}{距離}を30[cm]以上とすること。 |  | 2011_2,
24 | When measuring earth resistance using a direct-reading earth resistance meter, what is the appropriate placement of the two auxiliary earth electrodes P (for voltage) and C (for current) with respect to the earth electrode E to be measured? |  | Picture_24_A | Picture_24_B | Picture_24_C | Picture_24_D | 3 | ['配置(はいち)- Arrangement', '場合(ばあい)- Case; situation', '抵抗(ていこう)- Resistor', '接地(せっち)- Ground (electricity)'] | 直読式{接地}抵抗計を用いて、{接地}抵抗を{測定}する{場合}、被{測定}{接地}{極}Eに対する、2つの{補助}{接地}{極}P（{電圧}用）及びC（{電流}用）の{配置}として、{適切}なものは。 | Picture_24_A | Picture_24_B | Picture_24_C | Picture_24_D |  | 2011_2,
25 | What is not generally done when conducting a general inspection of low-voltage indoor wiring for general-use electric facilities? |  | Visual point of view | Insulation resistance measurement | Grounding resistance measurement | Conductor resistance measurement of indoor wiring | 4 | ['目視(もくし)- Seeing', '検査(けんさ)- Inspection', '低圧(ていあつ)- Low voltage'] | 一般用{電気}工{作物}の{低圧}{屋内配線}のしゅん工{検査}をする{場合}、一般に行われていないものは。 | 目視{点検} | {絶縁}抵抗{測定} | {接地}抵抗{測定} | {屋内配線}の{導体}抵抗{測定} |  | 2011_2,
26 | What is the most suitable method for measuring the insulation resistance between a low-voltage three-phase induction motor and ground using an insulation resistance tester? However, the L of the insulation resistance tester indicates the line terminal (line), and the E indicates the ground terminal (earth). |  | Picture_26_A | Picture_26_B | Picture_26_C | Picture_26_D | 3 | ['線路(せんろ)- Track; line', '端子(たんし)- Terminal (electricity)', '絶縁抵抗(ぜつえんていこう)- Insulation resistance'] | {絶縁}抵抗計を用いて、{低圧}{三相}{誘導電動機}と{大地}間の{絶縁}抵抗を{測定}する{方法}として、{適切}なものは。 ただし、{絶縁}抵抗計のLは{線}路{端子}（ライン）、Eは{接地}{端子}（{アース}）を{示す}。 | Picture_26_A | Picture_26_B | Picture_26_C | Picture_26_D |  | 2011_2,
27 | In a single-phase three-wire system 100/200V indoor wiring using three types of electric wires with red, white, and black insulation colors, the voltages between the wires and between the wires and the ground were measured. As a result, which voltage combination is suitable? However, the neutral point shall be white. |  | 200[V] between red wire and ground, 100[V] between white wire and ground, 0[V] between black wire and ground | 200[V] between red wire and black wire, 0[V] between white wire and ground [V], 100[V] between black wire and ground | 200[V] between red wire and white wire, 0[V] between red wire and ground, 100[V] between black wire and ground | between red wire and ground 100[V] between black wires, 0[V] between red wires and ground, 200[V] between black wires and ground | 2 | ['電線(でんせん)- Electric cable', '電圧(でんあつ)- Voltage', '種類(しゅるい)- Variety; kind', '被覆(ひふく)- Cover'] | {絶縁}{被覆}の色が{赤色}、白色、黒色の3{種類}の{電線}を{使用}した{単相}3線式100/200V{屋内配線}で、{電線}{相互}間及び{電線}と{大地}間の{電圧}を{測定}した。その{結果}として、{電圧}の{組合せ}で、{適切}なものは。 ただし、中性点は白色とする。 | {赤色}{線}と{大地}間200[V]、白色{線}と{大地}間100[V]、黒色{線}と{大地}間0[V] | {赤色}{線}と黒色{線}間200[V]、白色{線}と{大地}間0[V]、黒色{線}と{大地}間100[V] | {赤色}{線}と白色{線}間200[V]、{赤色}{線}と{大地}間0[V]、黒色{線}と{大地}間100[V] | {赤色}{線}と黒色{線}間100[V]、{赤色}{線}と{大地}間0[V]、黒色{線}と{大地}間200[V] |  | 2011_2,
28 | Anything that violates the Electrician Law. |  | Passed the electrician examination, but did not apply for the issuance of a license from the prefectural governor because he was not engaged in electrical work. | An electrician engaged in electrical work in multiple prefectures without notifying the Minister of Economy, Trade and Industry. | The electrician changed his address, but did not notify the prefectural governor within 30 days. | In order to prevent the electrician from losing his electrician's license, he kept it at the business office and engaged in electrical work. | 4 | ['複数(ふくすう)- Plural; multiple; several', '交付(こうふ)- Delivery', '電気工事(でんきこうじ)- Electrical work'] | {電気}{工事}士法に違反しているものは。 | {電気}{工事}士試験に合格したが、{電気}{工事}の{作業}に{従事}しないので都{道}府県知事に{免状}の交付申請をしなかった。 | {電気}{工事}士が経済産業大臣に届け出をしないで、複数の都{道}府県で{電気}{工事}の{作業}に{従事}した。 | {電気}{工事}士が{住所}を変更したが、30日以内に都{道}府県知事にこれを届け出なかった。 | {電気}{工事}士が{電気}{工事}士{免状}を紛失しないよう、これを営業所に保{管}したまま{電気}{工事}の{作業}に{従事}した。 |  | 2011_2,
29 | Under the Electrical Appliance and Material Safety Law, what are the specified electrical appliances and materials? |  | Fluorescent lamp with power consumption of 40[W] | Metal conduit tube with outer diameter of 19[mm] | Circuit breaker with rated current of 20[A] | Ventilation fan with power consumption of 30[W] | 3 | ['蛍光(けいこう)- Fluorescence', '適用(てきよう)- Applying'] | {電気}{用品}安全法において、{特定}{電気}{用品}の{適用}を受けるものは。 | 消費{電力}40[W]の蛍光ランプ | {外径}19[mm]の{金属}製{電線}{管} | {定格}{電流}20[A]の{配線}用{遮断器} | 消費{電力}30[W]の換気扇 |  | 2011_2,
30 | What is the correct statement regarding general electric equipment? |  | Electrical facilities that receive power at low voltage are considered general electric facilities even if an emergency backup generator with an output of 25 [kW] is installed in the same premises. | Equipment that receives power at low voltage is considered to be an electric facility for general use, even if a small-output power generation facility is installed on the same premises. | Even if it receives electricity at a high voltage, it may become a general-use electric facility depending on the type of industry where the demand is located. | Anything that receives high-voltage power is considered a general-purpose electric facility, regardless of the capacity of the received power or the type of industry in which it is demanded. | 2 | ['需要(じゅよう)- Demand', '非常用(ひじょうよう)- For emergency use', '低圧(ていあつ)- Low Voltage', '記述(きじゅつ)- Description', '作物(さくもつ)- Farm products', '電気工(でんきこう)- Electrician'] | 一般用{電気}工{作物}に関する{記述}として、{正しい}ものは。 | {低圧}で{受電}するものは、{出力}25[kW]の非常用予備{発電}装置を同一{構内}に{施設}しても一般用{電気}工{作物}となる。 | {低圧}で{受電}するものは、小{出力}{発電}{設備}を同一{構内}に{施設}しても、一般用{電気}工{作物}となる。 | {高圧}で{受電}するものであっても、{需要}{場所}の業{種}によっては、一般用{電気}工{作物}になる{場合}がある。 | {高圧}で{受電}するものは、{受電}{電力}の{容量}、{需要}{場所}の業{種}にかかわらず、すべて一般用{電気}工{作物}となる。 |  | 2011_2,
31 | What is the minimum allowable value [MΩ] for the insulation resistance between the electric circuit and the ground in the part indicated by ①? |  | 0.1 | 0.2 | 0.4 | 1 | 1 | ['最小値(さいしょうち)- Minimum value', '絶縁抵抗(ぜつえんていこう)- Insulation resistance', '電路(でんろ)- Electrical circuit '] | ①で{示す}{部分}の{電路}と{大地}間との{絶縁}抵抗と して、{許容}される{最小}{値} [MΩ] は。 | 0.1 | 0.2 | 0.4 | 1 |  | 2011_2,
32 | What is the minimum thickness diameter [mm] of mild steel wire (excluding cables) that can be used in the small force circuit shown in ②? |  | 0.5 | 0.8 | 1.2 | 1.6 | 2 | ['回路(かいろ)- Circuit', '直径(ちょっけい)- Diameter'] | ②で{示す}{部分}の小{勢力}{回路}で{使用}できる軟鋼{線} (ケーブルを除く)の{最小}太さの{直径}[mm] は。 | 0.5 | 0.8 | 1.2 | 1.6 |  | 2011_2,
33 | The part indicated by ③ is the outlet for the room air conditioner (rated 250V 20A). What is the correct pole arrangement (blade holder) for the outlet? |  | Picture_33_A | Picture_33_B | Picture_33_C | Picture_33_D | 4 | ['配置(はいち)- Arrangement', '定格(ていかく)- Rated value'] | ③で{示す}{部分}はルームエアコン ({定格}250V 20A)用{コンセント}である。 {コンセント}の{極}{配置} (刃受) で、{正しい}ものは。 | Picture_33_A | Picture_33_B | Picture_33_C | Picture_33_D |  | 2011_2,
34 | What is the purpose of using the equipment with the symbol shown in ④? |  | Cut off the unbalanced voltage. | Cut off the ground fault current. | Shut off overcurrent. | Breaks off overcurrent and ground fault current. | 3 | ['電流(でんりゅう)- Electric current', '電圧(でんあつ)- Volatge', '不平衡(ふへいこう)- Imbalance'] | ④で{示す}{図}{記号}の{器具}を用いる{目的}は。 | {不平衡}{電圧}を{遮断}する。 | 地絡{電流}を{遮断}する。 | 過{電流}を{遮断}する。 | 過{電流}と地絡{電流}とを{遮断}する。 |  | 2011_2,
35 | What is the name of the symbol shown in ⑤? |  | Watt meter | Time switch | Circuit breaker for wiring | Electricity meter | 4 | ['配線用遮断器(はいせんようしゃだんき)- Molded-case circuit breaker; MCCB', '電力計(でんりょくけい)- Wattmeter'] | ⑤で{示す}{図}{記号}の{名称}は。 | {電力}計 | タイム{スイッチ} | {配線}用{遮断器} | {電力}量計 |  | 2011_2,
36 | The part indicated by ⑥ is an automatic flasher for outdoor lights. What is the correct sidenote for the graphical symbol? |  | A(3A) | L(3A) | T(3A) | P(3A) | 1 | ['表示(ひょうじ)- Indication', '自動(じどう)- Automatic', '部分(ぶぶん)- portion'] | ⑥で{示す}{部分}は{屋外}灯の{自動}{点滅器}である。 {図}{記号}の傍記{表示}として、 {正しい}ものは。 | A(3A) | L(3A) | T(3A) | P(3A) |  | 2011_2,
37 | What is the maximum length [m] of the electric circuit between the house and the garage when the entrance switch shown in ⑦ can be omitted? |  | 8 | 10 | 15 | 20 | 3 | ['車庫(しゃこ)- Garage (house)', '住宅(じゅうたく)- Residence', '場合(ばあい)- Case'] | ⑦で{示す}引込口{開閉器}が{省略}できる{場合}の、 {住宅}と車庫との間の{電路}の{長さ}の{最大値} [m] は。 | 8 | 10 | 15 | 20 |  | 2011_2,
38 | What is the appropriate construction method for the part indicated by ⑧? |  | Cable construction using 600V vinyl-insulated vinyl-sheathed round cable Mouth. | Metal pipe work | Metal duct work | Metal wire work | 2 | ['円形(えんけい)- Round shape', '金属(きんぞく)- Metal', '円形(えんけい)- Round shape', '絶縁(ぜつえん)- Insulation'] | ⑧で{示す}{部分}の{工事}{方法}として、 {適切}なものは。 | 600Vビニル{絶縁}ビニルシースケーブル丸形を{使用}したケーブル{工事} | {金属}{管}{工事} | {金属}ダクト{工事} | {金属}{線}び{工事} |  | 2011_2,
39 | What is the minimum number of wires (number of core wires) for the part indicated by ⑨? However, wire the ground side wire from the power supply to the lighting equipment without going through the switch. |  | 3 | 4 | 5 | 6 | 2 | ['照明器具(しょうめいきぐ)- Lighting equipment', '電線(でんせん)- Electric cable', '部分(ぶぶん)- Portion'] | ⑨で{示す}{部分}の{最少}{電線}{本数}(心線数)は。 ただし{電源}からの{接地}側{電線}は、{スイッチ}を経由しないで照明{器具}に{配線}する。 | 3 | 4 | 5 | 6 |  | 2011_2,
40 | What is the name of the symbol shown in ⑩? |  | Implant | Hook ceiling (round) | Ceiling outlet (hook type) | Pendant | 2 | ['天井(てんじょう)- Ceiling', '器具(きぐ)- Utensil'] | ⑩で{示す}{図}{記号}の{名称}は。 | 埋込{器具} | 引掛シーリング(丸) | {天井}{コンセント} (引掛形) | ペンダント |  | 2011_2,
41 | ⑪ What is inappropriate for the construction of the joint box for VVF shown in (1) when crimping connection by ring sleeve E type? |  | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D | 2 | ['場合(ばあい)- Case; situation', '接続(せつぞく)- Connection', '工事(こうじ)- Construction work'] | ⑪で{示す} VVF 用ジョイントボックス{部分}の{工事}を、リングスリーブE 形による{圧着}{接続}で行う{場合}に用いるものとして、{不適切}なものは。 | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D |  | 2011_2,
42 | Equipment with the symbol shown in .⑫ |  | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D | 2 | ['記号(きごう)- Symbol'] | ⑫で{示す}{図}{記号}の{器具}は。 | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D |  | 2011_2,
43 | As for the equipment with the symbol shown in ⑬. However, the diagram below the photo shows the configuration of the contacts. |  | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D | 1 | ['構成(こうせい)- Composition', '器具(きぐ)- Utensil'] | ⑬で{示す}{図}{記号}の{器具}は。ただし、{写真}下の{図}は、{接点}の{構成}を{示す}。 | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D |  | 2011_2,
44 | What is the equipment with the symbol shown in ⑭? |  | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D | 4 | ['図(ず)- Drawing'] | ⑭で{示す}{図}{記号}の{器具}は。 | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D |  | 2011_2,
45 | The one that measures the ground resistance of the part indicated by ⑮. |  | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D | 4 | ['抵抗(ていこう)- Resistance'] | ⑮で{示す}{部分}の{接地}抵抗 を{測定}するものは。 | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D |  | 2011_2,
46 | Equipment to be attached to the part indicated by ⑯. |  | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D | 3 | ['部分(ぶぶん)- Portion'] | ⑯で{示す}{部分}に取り付け る{器具}は。 | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D |  | 2011_2,
47 | Items that will not be used in the construction of the part indicated by ⑰. |  | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D | 1 | ['使用(しよう)- Use'] | ⑰で{示す}{部分}の{工事}におい、{使用}されることのない ものは。 | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D |  | 2011_2,
48 | What tools will not be used in the construction of the part indicated by ⑱? |  | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D | 3 | ['工具(こうぐ)- Hand tool'] | ⑱で{示す}{部分}の{工事}において、{使用}されることの ない{工具}は。 | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D |  | 2011_2,
49 | In the joint box in the ceiling of the part indicated by ⑲, if all connections are crimp connections, what is the appropriate combination of the type and minimum number of ring sleeves to be used? |  | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D | 1 | ['種類(しゅるい)- Variety', '個数(こすう)- Quantity', '圧着(あっちゃく)- Pressure bonding', '接続(せつぞく)- Connection'] | ⑲で{示す}{部分}の{天井}内のジョイントボックス内において、{接続}をすべて{圧着}{接続}とする{場合}、{使用}するリングスリーブの{種類}と{最少}{個数}の{組合せ}で、{適切}なものは。 | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D |  | 2011_2,
50 | Equipment with graphical symbols shown in ⑳. |  | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D | 3 | ['示す(しめす)- To indicate'] | ⑳で{示す}{図}{記号}の{器具}は。 | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D |  | 2011_2,