## Sheet1
no | Eng | Picture | Option_1_Eng | Option_2_Eng | Option_3_Eng | Option_4_Eng | Ans | Vocab | Jpn | Option_1_Jpn | Option_2_Jpn | Option_3_Jpn | Option_4_Jpn | Exp | comment
1 | In the circuit shown in the figure, what is the combined resistance [Ω] between terminals a and b ? | Picture_1 | 1.0 | 1.2 | 1.8 | 2.0 | 2 | ['合成(ごうせい)- Synthesis', '端子(たんし)- Terminal (electricity)', '回路(かいろ)- Circuit'] | {図}のような{回路}で、{端子}a-b間の{合成}抵抗[Ω]は。 | 1.0 | 1.2 | 1.8 | 2.0 | (3×3)/(3+3) =1.5 ohms 3+3 = 6 ohms ( 1.5×6)/(1.5+6) = 1.2 Ω | 2012_1,
2 | In the circuit shown in the figure, when the current flowing through resistor R is 4[A] and the current flowing through reactance X is 3[A], the power consumption [W] of this circuit is: | Picture_2 | 300 | 400 | 500 | 700 | 2 | ['消費電力(しょうひでんりょく)- Electricity consumption', '電流(でんりゅう)- Electric current', '抵抗(ていこう)- Resistor'] | {図}のような{回路}で、抵抗Rに{流れる}{電流}が4[A]、リアクタンスXに{流れる}{電流}が3[A]であるとき、この{回路}の消費{電力}[W]は。 | 300 | 400 | 500 | 700 | Reactance X is a pseudo resistance that does not consume power. So, since only R consumes power, 100[V]*4[A]＝400[W] | 2012_1,
3 | What is the length [m] of an annealed copper wire with a diameter of 3.2 [mm] that has the same electric resistance as that of an annealed copper wire with a diameter of 1.6 [mm] and a length of 8 [m]? However, the resistivity of the annealed copper wire shall be the same. |  | 4 | 8 | 16 | 32 | 4 | ['抵抗率(ていこうりつ)- Resistivity', '銅線(どうせん)- Copper line', '直径(ちょっけい)- Diameter'] | {直径}1.6[mm]、{長さ}8[m]の軟{銅線}と{電気}抵抗が等しくなる{直径}3.2[mm]の軟{銅線}の{長さ}[m]は。ただし、軟{銅線}の{抵抗率}は同一とする。 | 4 | 8 | 16 | 32 | If the diameter or radius of the conductor is doubled, the electrical resistance will be 1/4. Quadrupling the length means 8 x 4 = 32 | 2012_1,
4 | What is the amount of electricity [kW·h] required to heat 60 liters of water by 20[°C] with an electric heater? However, the energy required to raise the temperature of 1 liter of water by 1[°C] is 4.2[kJ], and the thermal efficiency is 100[%]. |  | 1.0 | 1.2 | 1.4 | 1.6 | 3 | ['熱効率(ねつこうりつ)- Thermal efficiency', '温度(おんど)- Temperature', '電熱器(でんねつき)- electrothermic equipment'] | {電熱器}により、60リットルの水を20[°C]上昇させるのに{必要}な{電気}量[kW·h]は。ただし、1リットルの水の{温度}を1[°C]上昇させるのに{必要}なエネルギーは4.2[kJ]とし、{熱効率}は100[%]とする。 | 1.0 | 1.2 | 1.4 | 1.6 | 4.2*60*20 = 5040 [KJ]. Since KJ＝KW・s, when converted to KW・h, 5040[KW・s]/3600＝1.4KW・h | 2012_1,
5 | When a three-phase induction motor with rated voltage V [V] and rated current I [A] was operated continuously for time t [h], the power consumption was W [kW·h]. The formula for the power factor [%] of this motor is |  | Picture_5_A | Picture_5_B | Picture_5_C | Picture_5_D | 3 | ['力率(りきりつ)- Power factor', '誘導電動機(ゆうどうでんどうき)- Induction motor', '電圧(でんあつ)- Voltage', '定格(ていかく)- Rated value'] | {定格}{電圧}V[V]、{定格}{電流}I[A]の{三相}{誘導電動機}を{定格}{状態}で時間t[h]の間、連続運転したところ、消費{電力}量がW[kW·h]であった。この電動機の{力率}[%]を表す式は。 | Picture_5_A | Picture_5_B | Picture_5_C | Picture_5_D |  | 2012_1,
6 | Low-voltage indoor wiring work using synthetic resin flexible conduit (PF pipe), when three 600V vinyl insulated wires (copper conductors) with a cross-sectional area of ​​5.5 [mm²] are installed in the pipe, the permissible per wire Current [A] is However, the ambient temperature should be 30[°C] or less, and the current reduction factor should be 0.70. |  | 26 | 34 | 42 | 49 | 2 | ['係数(けいすう)- Coefficient', '許容(きょよう)- Permission', '電線(でんせん)- Electric cable', '絶縁(ぜつえん)- Insulation', '屋内配線(おくないはいせん)- Interior wiring', '低圧(ていあつ)- Low voltage'] | {合成}樹脂製可とう{電線}管（PF管）による{低圧}{屋内配線}{工事}で、{管内}に{断面積}5.5[mm²]の600Vビニル{絶縁}{電線}（銅{導体}）3本を収めて{施設}した{場合}、{電線}1本{当たり}の{許容}{電流}[A]は。ただし、{周囲}{温度}は30[°C]{以下}、{電流}{減少}{係数}は0.70とする。 | 26 | 34 | 42 | 49 | the allowable current is 49A, so 49 x 0.7 = 34.3 | 2012_1,
7 | In single-phase two-wire wiring as shown in the figure, the minimum wire thickness [mm²] to keep the line voltage drop below 1 [V] when a current of 10 [A] flows through a resistive load. teeth. However, the resistance of the wire shall be 0.02[Ω] per 1[mm²] cross-sectional area and 1[m] length. |  | 5.5 | 8 | 14 | 22 | 3 | ['断面積(だんめんせき)- Cross-sectional area', '電流(でんりゅう)- Electric current', '配線(はいせん)- Wiring', '単相(たんそう)- Single phase'] | {図}のような{単相}2線式{配線}において、抵抗{負荷}に10[A]の{電流}が流れたとき、線路の{電圧}降下を1[V]{以下}にするための{電線}の太さの{最小}{値}[mm²]は。ただし、{電線}の抵抗は、{断面積}1[mm²]、{長さ}1[m]{当たり}0.02[Ω]とする。 | 5.5 | 8 | 14 | 22 | 0.02×(35×2)／X×10＝1 1.4／X×10＝1 14X＝1 X＝14 | 2012_1,
8 | In the single-phase three-wire circuit shown in the figure, when the resistance per wire is 0.1 [Ω] and the current flowing through the resistive load is both 10 [A], the power loss [W] in this wire line is: |  | 10 | 20 | 30 | 40 | 2 | ['電流(でんりゅう)- Electric current', '抵抗(ていこう)- Resistance', '電線(でんせん)- Electric cable', '回路(かいろ)- Circuit'] | {図}のような{単相}3線式{回路}において、{電線}1線{当たり}の抵抗が0.1[Ω]、抵抗{負荷}に{流れる}{電流}がともに10[A]のとき、この{電線}路の{電力}損失[W]は。 | 10 | 20 | 30 | 40 | V = 10 x 0.1 = 1 Since V = 1V, P = 1 x 10 = 10W. There are two lines above and below, so 10W + 10W = 20W. | 2012_1,
9 | As shown in the figure, when branching from a low-voltage indoor main line protected by an overcurrent circuit breaker with a rated current of 60[A] and installing an overcurrent circuit breaker at a position of 7[m], the allowable current of the wire between a and b is The minimum value of [A] is . | Picture_9 | 21 | 33 | 42 | 60 | 1 | ['電線(でんせん)- Electric cable', '屋内(おくない)- Indoor', '遮断器(しゃだんき)- Circuit breaker', '過電流(かでんりゅう)- Over current'] | {図}のように{定格}{電流}60[A]の過{電流}{遮断器}で保護された{低圧}{屋内}{幹線}から{分岐}して、7[m]の{位置}に過{電流}{遮断器}を{施設}するとき、a-b間の{電線}の{許容}{電流}の{最小}{値}[A]は。 | 21 | 33 | 42 | 60 | The main line is 8m or less to the switch of the branch circuit, an overcurrent breaker that protects the main line Up to 35% of the rated current of the instrument is permitted. 60 × 0.35 = 21 | 2012_1,
10 | In branch circuits of low-voltage indoor wiring, what is the appropriate combination of circuit breakers, branch circuit wire thicknesses, and outlets? However, the distance from the branch point to the circuit breaker for wiring is 3[m], and the distance from the circuit breaker for wiring to the outlet is 8[m]. |  | Picture_10_A | Picture_10_B | Picture_10_C | Picture_10_D | 4 | ['配線用遮断器(はいせんようしゃだんき)- Molded-case circuit breaker; MCCB', '分岐(ぶんき)- Divergence', '回路(かいろ)- Circuit'] | {低圧}{屋内配線}の{分岐}{回路}において、配線用{遮断器}、{分岐}{回路}の{電線}の太さ及び{コンセント}の{組合せ}として、{適切}なものは。ただし、{分岐}点から配線用{遮断器}までは3[m]、配線用{遮断器}から{コンセント}までは8[m]とし、{電線}の{数値}は{分岐}{回路}の{電線}（軟{銅線}）の太さを{示す}。 | Picture_10_A | Picture_10_B | Picture_10_C | Picture_10_D |  | 2012_1,
11 | What is the purpose of the entrance cap? |  | Used to block the end of floor ducts. | Used to prevent concrete from entering the metal pipe when concrete is poured. | Used for parts where pipes bend at right angles in metal pipe work. | It is mainly used to prevent rainwater from entering by attaching it to the upper end of a vertical metal pipe. | 4 | ['金属(きんぞく)- Metal', '工事(こうじ)- Construction work', '終端部(しゅうたんぶ)- Trailer'] | エン{トランス}キャップの{使用}{目的}は。 | フロアダクトの{終端部}を閉そくするために{使用}する。 | コンクリート打ち込み時に{金属}{管内}にコンクリートが浸入するのを防止するために{使用}する。 | {金属}{管}{工事}で{管}が{直角}に屈曲する{部分}に{使用}する。 | 主として垂直な{金属}{管}の上端部に取り付けて、雨水の侵入を防止するために{使用}する。 |  | 2012_1,
12 | What is the role of the zero-phase current transformer built into the earth leakage breaker? |  | Ground fault current detection | Short circuit current detection | Overvoltage detection | Undervoltage detection | 1 | ['検出(けんしゅつ)- Detection', '役割(やくわり)- Role; duties', '変流器(へんりゅうき)- Transformer'] | {漏電}{遮断器}に内蔵されている零相{変流器}の{役割}は。 | 地絡{電流}の{検出} | 短絡{電流}の{検出} | 過{電圧}の{検出} | {不足}{電圧}の{検出} |  | 2012_1,
13 | What is the purpose of connecting a low-voltage phase-advancing capacitor in parallel to a low-voltage three-phase induction motor? |  | Prevent motor vibration. | Improve the power factor of the circuit. | Prevent fluctuations in rotation speed. | Prevent power frequency fluctuations. | 2 | ['周波数(しゅうはすう)- Frequency', '回転(かいてん)- Rotation', '振動(しんどう)- Oscillation', '低圧(ていあつ)- Low voltage'] | {低圧}{三相}{誘導電動機}に対して{低圧}進相コンデンサを{並列}に{接続}する{目的}は。 | {電動機}の{振動}を防ぐ。 | {回路}の{力率}を改善する。 | {回転}{速度}の変動を防ぐ。 | {電源}の{周波数}の変動を防ぐ。 |  | 2012_1,
14 | The electrical machine with the best power factor. |  | Electric toaster | Electric washing machine | Electric refrigerator | LED light bulb (with built-in controller) | 1 | ['器具(きぐ)- Tool; instrument', '力率(りきりつ)-Power Fector'] | {力率}の最もよい{電気}{機械}{器具}は。 | {電気}トースター | {電気}洗濯機 | {電気}冷蔵庫 | LED{電球}（制御装置内蔵形） |  | 2012_1,
15 | What is the name of the tool shown in the photo? | Picture_15 | Manual hydraulic compressor | Manual hydraulic cutter | Knockout puncher (hydraulic) | Manual hydraulic crimper | 4 | ['問題(もんだい)- Question ', '写真(しゃしん)- Photograph'] | {写真}に{示す}{工具}の{名称}は。 | {手動}油圧式圧縮器 | {手動}油圧カッタ | ノックアウトパンチャ（油圧式） | {手動}油圧式{圧着}器 |  | 2012_1,
16 | What is the purpose of the tool shown in the photo? | Picture_16 | Used to bend thick wires. | Used to prevent slippage such as rotation of conduit during construction. | Used as a branch line for electric wires. | Used to adjust the slack of the overhead wire. | 4 | ['画像(がぞう)- Image', '用途(ようと)- Purpose'] | {写真}に{示す}{工具}の{用途}は。 | {太い}{電線}を曲げてくせをつけるのに用いる。 | {施工}時の{電線}{管}の{回転}等すべり止めに用いる。 | {電線}の支線として用いる。 | 架空{線}のたるみを調整するのに用いる。 |  | 2012_1,
17 | The photo shows the name of the appliance. | Picture_17 | Earth leakage alarm | Electromagnetic switch | Earth leakage circuit breaker | Wiring circuit breaker (for motor protection) | 4 | ['開閉器(かいへいき)-Switch', '漏電(ろうでん)- Short circuit'] | {写真}に{示す}{器具}の{名称}は。 | {漏電}{警報器} | {電磁}{開閉器} | {漏電}{遮断器} | {配線}用{遮断器}（{電動機}保護{兼用}） |  | 2012_1,
18 | What is the name of the material indicated by the arrow in the photo? | Picture_18 | Cable rack | Metal duct | Cellular duct | Floor duct | 1 | ['金属(きんぞく)- Metal', '矢印(やじるし)- Arrow (symbol)'] | {写真}の{矢印}で{示す}{材料}の{名称}は。 | ケーブルラック | {金属}ダクト | セルラダクト | フロアダクト |  | 2012_1,
19 | What is inappropriate as a construction method for low-voltage indoor wiring with a working voltage of 300 [V] or less? |  | In flexible metal conduit work, stranded wires (600V vinyl insulated wires) were used, and were housed without connecting parts inside the pipe. | In the lighting duct construction, the opening of the duct was installed facing upward. | When branching electric wires during floor duct work, the joints were covered with sufficient insulation, and the joints were housed in a junction box so that they could be easily inspected. | When branching electric wires in metal duct construction, the joints were covered with sufficient insulation, and the joints were placed in the duct so that they could be easily inspected. | 2 | ['管内(かんない)- In a pipe', '接続(せつぞく)- Connection', '部分(ぶぶん)- Portion; section'] | {使用}{電圧}300[V]{以下}の{低圧}{屋内配線}の{工事}{方法}として、{不適切}なものは。 | {金属}可とう{電線}管{工事}で、{より線}（600Vビニル{絶縁}{電線}）を用いて、{管内}に{接続}{部分}を設けないで収めた。 | ライティングダクト{工事}で、ダクトの開口部を上に向けて{施設}した。 | フロアダクト{工事}で、{電線}を{分岐}する{場合}、{接続}{部分}に十分な{絶縁}{被覆}を施し、かつ、{接続}{部分}を{容易}に{点検}できるようにして{接続}箱（ジャンクションボックス）に収めた。 | {金属}ダクト{工事}で、{電線}を{分岐}する{場合}、{接続}{部分}に十分な{絶縁}{被覆}を施し、かつ、{接続}{部分}を{容易}に{点検}できるようにしてダクトに収めた。 |  | 2012_1,
20 | Inappropriate construction of low-voltage indoor wiring in places where petroleum is stored. |  | Synthetic resin pipe work installed so that there is no risk of damage (excluding synthetic resin conduits and CD pipes with a thickness of less than 2 [mm]) | Metal pipe work using thin steel conduit | Cable work using MI cable | Cable work using 600V cross-linked polyethylene insulated vinyl sheath cable without housing it in a protective device | 4 | ['絶縁(ぜつえん)- Insulation', '架橋(かきょう)- Dridge-building', '損傷(そんしょう)- Damage'] | 石油類を貯蔵する{場所}における{低圧}{屋内配線}の{工事}で、{不適切}なものは。 | {損傷}を受けるおそれのないように{施設}した{合成}樹脂{管}{工事}（{厚さ}2[mm]未満の{合成}樹脂製{電線}{管}及びCD{管}を除く） | 薄鋼{電線}{管}を{使用}した{金属}{管}{工事} | MIケーブルを{使用}したケーブル{工事} | 600V{架橋}ポリエチレン{絶縁}ビニルシースケーブルを{防護}装置に収めないで{使用}したケーブル{工事} |  | 2012_1,
21 | In low-voltage indoor wiring work using 600V vinyl-insulated vinyl-sheathed flat cables of 1.6 [mm], what is inappropriate for the insulation treatment of the end connections between insulated wires? However, the vinyl tape shall be an insulating tape with a thickness of about 0.2 [mm] specified by JIS. |  | Connected with a ring sleeve, and wrapped once (2 layers) with vinyl tape over half the width of the connection. | Connected with a ring sleeve, and wrapped twice (4 layers) with black adhesive polyethylene insulating tape (thickness: about 0.5 [mm]) over half the width. | Connect with a ring sleeve, wrap the connecting part with self-adhesive insulating tape (thickness of about 0.5 [mm]) once (two layers) by overlapping at least half the width, and then wrap it once (two layers) with protective tape (thickness of about 0.2 [mm]). ) was overlapped by more than half the width and wound once (2 layers). | Connection was made using a plug-in connector, and the connecting part was not wrapped with vinyl tape. | 1 | ['接続(せつぞく)- Connection ', '相互(そうご)- Mutual; reciprocal', '低圧(ていあつ)- Low voltage'] | 600Vビニル{絶縁}ビニルシースケーブル平形1.6[mm]を{使用}した{低圧}{屋内配線}{工事}で、{絶縁}{電線}{相互}の{終端}{接続}{部分}の{絶縁}処理として、{不適切}なものは。ただし、ビニルテープはJISに定める{厚さ}約0.2[mm]の{絶縁}テープとする。 | リングスリーブにより{接続}し、{接続}{部分}をビニルテープで{半幅}以上重ねて1回（2層）巻いた。 | リングスリーブにより{接続}し、{接続}{部分}を黒色粘着性ポリエチレン{絶縁}テープ（{厚さ}約0.5[mm]）で{半幅}以上重ねて2回（4層）巻いた。 | リングスリーブにより{接続}し、{接続}{部分}を自己融着性{絶縁}テープ（{厚さ}約0.5[mm]）で{半幅}以上重ねて1回（2層）巻き、更に保護テープ（{厚さ}約0.2[mm]）を{半幅}以上重ねて1回（2層）巻いた。 | 差込形{コネクタ}により{接続}し、{接続}{部分}をビニルテープで巻かなかった。 |  | 2012_1,
22 | When using a 600V vinyl insulated wire in a metal pipe for low-voltage indoor wiring work, the current reduction factor for obtaining the allowable current of the wire is calculated by combining the number of wires in the same pipe and the current reduction factor of the wire. what is wrong. However, the ambient temperature should be 30[°C] or less. |  | 2本 0.80 | 4本 0.63 | 5本 0.56 | 6本 0.56 | 1 | ['減少(げんしょう)- Decrease', '係数(けいすう)- Coefficient', '電流(でんりゅう)- Electric current'] | {低圧}{屋内配線}{工事}で、600Vビニル{絶縁}{電線}を{金属}管に収めて{使用}する{場合}、その{電線}の{許容}{電流}を求めるための{電流}{減少}{係数}{に関して}、同一{管内}の{電線}数と{電線}の{電流}{減少}{係数}との{組合せ}で、誤っているものは。ただし、{周囲}{温度}は30[°C]{以下}とする。 | 2本 0.80 | 4本 0.63 | 5本 0.56 | 6本 0.56 |  | 2012_1,
23 | For single-phase 100[V] indoor wiring, is there a fixture that can be directly attached to a 100[V] base E26 LED light bulb? |  | Lamp receptacle | Straight tube fluorescent lamp fixture | Circular fluorescent lamp fixture | Hanging ceiling rosette | 1 | ['蛍光灯(けいこうとう)- Fluorescent lamp', '電球(でんきゅう)- light bulb', '口金(くちがね)- Socket (for light, etc.)'] | {単相}100[V]の{屋内配線}{工事}で、{口金}E26の100[V]用LED{電球}を{直接}取り付けることができる{器具}は。 | ランプレセプタクル | 直{管}形{蛍光灯}{器具} | {円形}{蛍光灯}{器具} | 引掛シーリングローゼット |  | 2012_1,
24 | Since it was difficult to measure the insulation resistance in an electric circuit where the working voltage is low, we confirmed the insulation performance by measuring the leakage current with the working voltage applied. What is the maximum value [mA] of leakage current that can be judged to have the insulation performance specified in "Interpretation of Technical Standards for Electrical Equipment"? |  | 0.1 | 0.2 | 1 | 2 | 3 | ['最大値(さいだいち)- Greatest value', '技術基準(ぎじゅつきじゅん)- Technical standards', '状態(じょうたい)- State; condition', '測定(そくてい)- Measurement', '電圧(でんあつ)- Voltage'] | {使用}{電圧}が{低圧}の{電路}において、{絶縁}抵抗の{測定}が困難であったため、{使用}{電圧}が加わった{状態}で漏えい{電流}により{絶縁}{性能}を{確認}した。「{電気}{設備}の{技術基準}の{解釈}」に定める{絶縁}{性能}を有していると{判断}できる漏えい{電流}の{最大値}[mA]は。 | 0.1 | 0.2 | 1 | 2 |  | 2012_1,
25 | What is the correct measurement method for measuring the leakage current of a single-phase three-wire circuit using a clamp-type leakage current meter? However, the shaded area indicates the neutral line. |  | Picture_25_A | Picture_25_B | Picture_25_C | Picture_25_D | 4 | ['電流計(でんりゅうけい)- Ammeter', '測定方法(そくていほうほう)- Measuring method', '回路(かいろ)- Circuit'] | {単相}3{線}式{回路}の漏れ{電流}を、クランプ形漏れ{電流}計を用いて{測定}する{場合}の{測定}{方法}として、{正しい}ものは。ただし、斜{線}部は中性{線}を{示す}。 | Picture_25_A | Picture_25_B | Picture_25_C | Picture_25_D |  | 2012_1,
| What are the incorrect statements regarding the use of the measuring instrument? |  | Measure the load current with a clamp-type ammeter. | Conduct a continuity test with a circuit meter. | Measure the rotation speed of the motor with a tachometer. | Check the phase sequence (phase rotation) of the three-phase alternating current with a voltage detector. | 4 | ['回転(かいてん)- Rotation', '回路計(かいろけい)- Multimeter', '記述(きじゅつ)- Description', '用途(ようと)- Use; service'] | {測定}器の{用途}に関する{記述}として、誤っているものは。 | クランプ形{電流}計で{負荷}{電流}を{測定}する。 | {回路}計で{導通}試験を行う。 | {回転}計で{電動機}の{回転}{速度}を{測定}する。 | {検電器}で{三相}{交流}の相順（相{回転}）を調べる。 |  | 2012_1,
27 | We measured the insulation resistance between the electric circuit of the low-voltage indoor wiring and the ground. Those that do not conform to the "Ministerial Ordinance for Establishing Technical Standards for Electrical Equipment". |  | We measured the insulation resistance of a single-phase three-wire 100/200V motor circuit with a working voltage of 200[V] and found that it was 0.12[MΩ]. | We measured the insulation resistance of the three-phase, three-wire system with a working voltage of 200 [V] (voltage to ground: 200 [V]) and found that the insulation resistance was 0.18 [MΩ]. | When I measured the insulation resistance of the single-phase two-wire low-voltage indoor wiring with a working voltage of 100 [V] on the distribution board, it was 1.2 [MΩ], so I measured the individual branch circuits. omitted. | We measured the insulation resistance of the single-phase two-wire system with a working voltage of 100 [V] and found that it was 2.1 [MΩ]. | 2 | ['対地(たいち)- Ground to ground', '電動機(でんどうき)- Electric motor', '電圧(でんあつ)- Voltage', '電路(でんろ)- Electrical circuit'] | {低圧}{屋内配線}の{電路}と{大地}間の{絶縁}抵抗を{測定}した。「{電気}{設備}に関する{技術基準}を定める{省令}」に適合していないものは。 | {単相}3{線}式100/200Vの{使用}{電圧}200[V]{電動機}{回路}の{絶縁}抵抗を{測定}したところ、0.12[MΩ]であった。 | {三相}3{線}式の{使用}{電圧}200[V]（{対地}{電圧}200[V]）{電動機}{回路}の{絶縁}抵抗を{測定}したところ、0.18[MΩ]であった。 | {単相}2線式の{使用}{電圧}100[V]{低圧}{屋内配線}の{絶縁}抵抗を、{分電盤}で各{回路}を一括して{測定}したところ、1.2[MΩ]であったので個別{分岐}{回路}の{測定}を{省略}した。 | {単相}2{線}式の{使用}{電圧}100[V]{電灯}{分岐}{回路}の{絶縁}抵抗を{測定}したところ、2.1[MΩ]であった。 |  | 2012_1,
28 | According to the Electrician Law, what kind of work can only be done by an electrician in the work of electric facilities for general use? |  | Secondary side wiring work for small transformers (secondary voltage 36 [V] or less) used in intercom facilities | Installation of poles and brackets to support wires | Thread cutting of conduits , work to connect conduits and boxes | work to install electricity meters | 3 | ['作業(さぎょう)- Work', '電線(-でんせん)- Electric cable', '腕木(うでぎ)- Bracket'] | {電気}{工事}士法において、一般用{電気}工{作物}の{作業}で、{電気}{工事}士でなければ{従事}できない{作業}は。 | インターホーンの{施設}に{使用}する{小型}{変圧器}（二次{電圧}36[V]{以下}）の二次側{配線}{工事}の{作業} | {電線}を支持する柱、{腕木}を{設置}する{作業} | {電線}{管}をねじ切りし、{電線}{管}とボックスを{接続}する{作業} | {電力}量計の取り付け{作業} |  | 2012_1,
29 | What are the incorrect descriptions of specific electrical appliances under the Electrical Appliance and Material Safety Law? |  | A person who engages in the business of manufacturing Electrical Appliances and Materials may affix the label shown on the right to the specific Electrical Appliances and Materials that he or she has manufactured, provided that certain requirements are met. <PSE> | A person who imports electrical appliances may affix the label shown on the right to the specific imported electrical appliances if certain requirements are met. (PSE) | A person engaged in the business of selling Electrical Appliances and Materials shall not sell Specified Electrical Appliances and Materials that do not have the label specified by laws and regulations, except in cases where approval has been obtained from the Minister of Economy, Trade and Industry. | Electrical workers shall not use specified electrical appliances and materials that are not labeled as stipulated by laws and regulations for electrical work, except when approved by the Minister of Economy, Trade and Industry. | 2 | ['用品(ようひん)- Articles', '要件(ようけん)- Requirement', '事業(じぎょう)- Project', '記述(きじゅつ)- Description', '用品(ようひん)- Articles', '特定(とくてい)- Specific'] | {電気}{用品}安全法における{特定}{電気}{用品}に関する{記述}として、誤っているものは。 | {電気}{用品}の{製造}の{事業}を行う者は、一定の{要件}を満たせば{製造}した{特定}の{電気}{用品}に右記の{表示}を付けることができる。<PSE> | {電気}{用品}の{輸入}の{事業}を行う者は、一定の{要件}を満たせば{輸入}した{特定}の{電気}{用品}に右記の{表示}を付けることができる。 (PSE) | {電気}{用品}の{販売}の{事業}を行う者は、経済産業大臣の承認を受けた{場合}等を除き、{法令}に定める{表示}のない{特定}{電気}{用品}を{販売}してはならない。 | {電気}{工事}士は、経済産業大臣の承認を受けた{場合}等を除き、{法令}に定める{表示}のない{特定}{電気}{用品}を{電気}{工事}に{使用}してはならない。 |  | 2012_1,
30 | What is the correct combination of low voltage categories in the "Ministerial Ordinance for Establishing Technical Standards for Electrical Equipment"? |  | AC 750[V] or less, DC 600[V] or less | AC 600[V] or less, DC 600[V] or less | AC 600[V] or less, DC 750[V] or less | AC 600[ V] or less, DC 700 [V] or less | 3 | ['直流(ちょくりゅう)- Direct current; DC', '交流(こうりゅう)- Exchange', '電圧(でんあつ)- Voltage', '電気設備(でんきせつび)- Electrical equipment'] | 「{電気}{設備}に関する{技術基準}を定める{省令}」における{電圧}の{低圧}区分の{組合せ}で、{正しい}ものは。 | {交流}750[V]{以下}、{直流}600[V]{以下} | {交流}600[V]{以下}、{直流}600[V]{以下} | {交流}600[V]{以下}、{直流}750[V]{以下} | {交流}600[V]{以下}、{直流}700[V]{以下} |  | 2012_1,
31 | What is the name of the graphic symbol indicated by ①? |  | Pressure switch | Push button for electromagnetic switch | Push button | Grip push button | 2 | ['電磁(でんじ)- Electromagnetic', '圧力(あつりょく)- Pressure'] | ①で{示す}{図}{記号}の{名称}は。 | {圧力}{スイッチ} | {電磁}{開閉器}用押しボタン | 押しボタン | 握り押しボタン |  | 2012_1,
32 | Which of the following is the correct purpose for using the equipment with the symbol shown in ②? |  | Shut off overcurrent. | Cut off the ground fault current. | Cut off overcurrent and ground fault current. | Cut off the unbalanced current. | 1 | ['過電流(かでんりゅう)- Over current', '電流(でんりゅう)- Electric current'] | ②で{示す}{図}{記号}の{器具}を用いる{目的}のなかで{正しい}ものは。 | 過{電流}を{遮断}する。 | 地絡{電流}を{遮断}する。 | 過{電流}と地絡{電流}を{遮断}する。 | {不平衡}{電流}を{遮断}する。 |  | 2012_1,
33 | What is the indication attached to the symbol of the outdoor unit in the part of ③? |  | B | I | R | O | 4 | ['屋外(おくがい)- Outdoors;'] | ③の{部分}において{屋外}ユニットの{図}{記号}に傍記 する{表示}は。 | B | I | R | O |  | 2012_1,
34 | What is the minimum number of wires (number of core wires) in the part of ④? However, wire the ground side wire from the power supply to the lighting equipment without going through the switch. |  | 3 | 4 | 5 | 6 | 2 | ['電源(でんげん)- Electrical power', '電線(でんせん)- Electric cable'] | ④の{部分}の{最少}{電線}{本数}(心線数)は。ただし、{電源}からの{接地}側{電線}は、{スイッチ}を経由しないで照明{器具}に{配線}する。 | 3 | 4 | 5 | 6 |  | 2012_1,
35 | In the electric circuit in ⑤, the switch cannot be omitted at the lead-in port of the warehouse. |  | 8 | 10 | 15 | 20 | 3 | ['省略(しょうりゃく)- Omission', '倉庫(そうこ)- Warehouse'] | ⑤の{部分}の{電路}で{倉庫}の引込口に{開閉器}が {省略}できないのは、 {電路}の{長さ}が何メートルイ.8 を超える{場合}か。 | 8 | 10 | 15 | 20 |  | 2012_1,
36 | ⑥ What is the maximum value [A] of the rated current of the overload protection device? |  | 15 | 20 | 30 | 40 | 2 | ['保護装置(ほごそうち)- Safeguard', '過負荷(かふか)- Overload'] | ⑥ の{部分}の{過負荷}{保護装置}の{定格}{電流}の [{最大値} [A] は。 | 15 | 20 | 30 | 40 |  | 2012_1,
37 | What is the name of the symbol shown in ⑦? |  | Earth leakage breaker (with overload protection) | earth leakage alarm | Motor breaker | Circuit breaker for wiring | 1 | ['配線用遮断器(はいせんようしゃだんき)- Molded-case circuit breaker; MCCB', '警報器(けいほうき)- Alarm', '漏電(ろうでん)- Short circuit'] | ⑦で{示す}{図}{記号}の{名称}は。 | {漏電}{遮断器} ( {過負荷}保護付) | {漏電}{警報器} | モータブレーカ | {配線}用{遮断器} |  | 2012_1,
38 | What is used in ⑧? |  | Mercury lamp | Metal halide lamp | Sodium lamp | Fluorescent lamp | 3 | ['蛍光灯(けいこうとう)- Fluorescent lamp', '水銀灯(すいぎんとう)- Mercury lamp'] | ⑧で{使用}するものは。 | {水銀灯} | メタルハライド灯 | ナトリウム灯 | {蛍光灯} |  | 2012_1,
39 | What is the pole arrangement (blade holder) of the outlet used for the part indicated by ⑨? |  | Picture_39_A | Picture_39_B | Picture_39_C | Picture_39_D | 2 | ['配置(はいち)- Arrangement', '部分(ぶぶん)- Portion'] | ⑨で{示す}{部分}に{使用}する{コンセント}の{極}{配置}(刃受) は。 | Picture_39_A | Picture_39_B | Picture_39_C | Picture_39_D |  | 2012_1,
40 | What is the appropriate combination of the maximum value of the grounding resistance of the grounding work shown in ⑩ and the minimum thickness of the wire (annealed copper wire)? |  | 100(Ω) 1.6(mm) | 300(Ω) 1.6(mm) | 500(Ω) 1.6(mm) | 600(Ω) 2.0(mm) | 3 | ['最大値(さいだいち)- Global maximum', '接地(せっち)- Ground (electricity)'] | ⑩で{示す}{部分}の{接地}{工事}の{接地}抵抗の{最大値} と、{電線} (軟{銅線}) の{最小}太さとの{組合せ}で、{適切}なものは。 | 100(Ω) 1.6(mm) | 300(Ω) 1.6(mm) | 500(Ω) 1.6(mm) | 600(Ω) 2.0(mm) |  | 2012_1,
41 | The one with the symbol shown in ⑪. |  | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D | 1 | ['記号(きごう)- Symbol'] | ⑪で{示す}{図}{記号}のものは。 | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D |  | 2012_1,
42 | As for the equipment with the symbol shown in ⑫. |  | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D | 4 | ['器具(きぐ)- Tool'] | ⑫で{示す}{図}{記号}の{器具}は。 | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D |  | 2012_1,
43 | What is not used in the wiring work of the part indicated by ⑬? |  | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D | 3 | ['配線工事(はいせんこうじ)- Wiring work'] | ⑬で{示す}{部分}の{配線}{工事}で、{使用}されることのない ものは。 | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D |  | 2012_1,
44 | If all connections in the joint box shown in ⑭ are crimp connections, what is the appropriate combination of ring sleeve type and minimum number to be used? However, wire the ground side wire from the power supply to the lighting equipment without going through the switch. |  | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D | 3 | ['最少(さいしょう)- Lowest', '種類(しゅるい)- Variety', '接続(せつぞく)- Connection'] | ⑭で{示す}ジョイントボックス内の{接続}をすべて{圧着}接 ¦続とする{場合}、 {使用}するリ ングスリーブの{種類}と{最少} {個数}の{組合せ}で、{適切}なものは。ただし、{電源}からの{接地}側 {電線}は、{スイッチ}を経由し ないで照明{器具}に{配線}す る。 | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D |  | 2012_1,
45 | What tools are not suitable for pressure bonding the joint box shown in ⑮ with a ring sleeve E type crimp connection? |  | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D | 3 | ['工具(こうぐ)- Hand tool', '圧着(あっちゃく)- Pressure bonding'] | ⑮で{示す}ジョイントボックス{部分}の{工事}を、リングスリーブE形による{圧着}接¦続で行う{場合}に用いる{工具}として、{不適切}なものは。 | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D |  | 2012_1,
46 | What measures the insulation resistance of the circuit shown in ⑯? |  | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D | 1 | ['絶縁抵抗(ぜつえんていこう)- Insulation resistance', '回路(かいろ)- Circuit'] | ⑯で{示す}{回路}の{絶縁}抵抗を{測定}するものは。 | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D |  | 2012_1,
47 | As for the equipment with the symbol shown in ⑰. |  | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D | 4 | ['記号(きごう)- symbol'] | ⑰で{示す}{図}{記号}の{器具}は。 | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D |  | 2012_1,
48 | ⑱ What is used for the equipment with the symbol shown in ⑱? |  | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D | 2 | ['器具(きぐ)- Utensil', '使用(しよう)- Use'] | ⑱で{示す}{図}{記号}の{器具}に{使用}されているものは。 | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D |  | 2012_1,
49 | The part indicated by ⑲ used to support the pipe. |  | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D | 1 | ['部分(ぶぶん)- Portion'] | ⑲で{示す}{部分}で{管}の支持に{使用}されるものは。 | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D |  | 2012_1,
50 | Equipment used for the part indicated by ⑳. |  | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D | 4 | ['器具(きぐ)- Utensil'] | ⑳で{示す}{部分}に{使用}される {器具}は。 | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D |  | 2012_1,