## Sheet1
no | Eng | Picture | Option_1_Eng | Option_2_Eng | Option_3_Eng | Option_4_Eng | Ans | Vocab | Jpn | Option_1_Jpn | Option_2_Jpn | Option_3_Jpn | Option_4_Jpn | Exp | comment
1 | In the DC circuit shown in the figure, the voltage [V] between a and b is | Picture_1 | 10 | 20 | 30 | 40 | 2 | ['電圧(でんあつ)- Voltage', '直流回路(ちょくりゅうかいろ)- Direct-current circuit'] | {図}のような{直流}{回路}で，a - b 間の{電圧} [V] は。 | 10 | 20 | 30 | 40 | 100V + 100V = 200V 200V/20Ω+300Ω=4A 4A x 20Ω = 80V 100V - 80V = 20V | 2013_1,
2 | There are two copper wires of the same material, A and B. A has a diameter of 1.6 [mm] and a length of 20 [m], and B has a diameter of 3.2 [mm] and a length of 40 [m]. How many times is the resistance of A greater than the resistance of B? |  | 1 | 2 | 3 | 4 | 2 | ['抵抗(ていこう)- Resistance', '直径(ちょっけい)- Diameter', '銅線(どうせん)- Copper line', '材質(ざいしつ)- Material'] | A，B 2 本の同{材質}の{銅線}がある。A は{直径} 1.6 [mm]，{長さ} 20 [m]，B は{直径} 3.2 [mm]，{長さ} 40 [m] である。A の抵抗は B の抵抗の何倍か。 | 1 | 2 | 3 | 4 | RA = ρ (4×20/π×1.62) = 31.25ρ/π RB = ρ (4×40/π×3.22 = 15.625ρ/π | 2013_1,
3 | In the AC circuit shown in the figure, when the voltage across the resistor is 80 [V] and the voltage across the reactance is 60 [V], the power factor [%] of the load is: | Picture_3 | 43 | 57 | 60 | 80 | 4 | ['電圧(でんあつ)- Voltage', '両端(りょうたん)- Both ends', '回路(かいろ)- Circuit', '交流(こうりゅう)- Exchange'] | {図}のような{交流}{回路}で，抵抗の{両端}の{電圧}が 80 [V]，リアクタンスの{両端}の{電圧}が 60 [V] であるとき，{負荷}の{力率} [%] は。 | 43 | 57 | 60 | 80 | cosθ = 80/√802 + 602 = 0.80 | 2013_1,
4 | In the AC circuit shown in the figure, a capacitor C was installed to the load to improve the power factor to 100%. What is the indicated value of the ammeter at this time? | Picture_4 | Become zero. | Increase compared to before installing the capacitor. | Reduced compared to before installation of the capacitor. | There is no change compared to before the capacitor was installed. | 3 | ['電流計(でんりゅうけい)- Ammeter', '負荷(ふか)- Load', '交流(こうりゅう)- Exchange'] | {図}のような{交流}{回路}で，{負荷}に対してコンデンサ C を{設置}して，{力率}を 100 [%] に改善した。このときの{電流}計の{指示}{値}は。 | 零になる。 | コンデンサ{設置}前と比べて{増加}する。 | コンデンサ{設置}前と比べて{減少}する。 | コンデンサ{設置}前と比べて変化しない。 |  | 2013_1,
5 | In the 3-phase 3-wire 200 [V] circuit shown in the figure, the resistance between c and o was disconnected. Voltage between a and o before and after disconnection V. What is the correct combination of V values ​​[V]? | Picture_5 | 116 before disconnection, 100 after disconnection | 116 before disconnection, 116 after disconnection | 100 before disconnection, 116 after disconnection | 100 before disconnection, 100 after disconnection | 1 | ['断線(だんせん)- Disconnection', '電圧(でんあつ)- Voltage', '抵抗(ていこう)- Resistance', '回路(かいろ)- Circuit', '三相(さんそう)- Three phases'] | {図}のような{三相} 3 線式 200 [V] の{回路}で c - o 間の抵抗が{断線}した。{断線}前と{断線}後の a - o 間の{電圧} V の{値} [V] の{組合せ}として{正しい}ものは。 | {断線}前 116，{断線}後 100 | {断線}前 116，{断線}後 116 | {断線}前 100，{断線}後 116 | {断線}前 100，{断線}後 100 | 200/√3 = 116 [V] 200/2 = 100 [V] | 2013_1,
6 | In the single-phase two-wire circuit shown in the figure, when the voltage between c and c' is 100 [V], the voltage [V] between a and a' is: however, r Let r be the wire resistance [Ω]. | Picture_6 | 100 | 102 | 103 | 104 | 4 | ['電圧(でんあつ)- Voltage', '電線(でんせん)- Electric cable', '回路(かいろ)- Circuit', '単相(たんそう)- Single phase'] | {図}のような{単相} 2 線式{回路}で，c - c' 間の{電圧}が 100 [V] のとき，a - a' 間の{電圧} [V] は。ただし， r は{電線}の抵抗 [Ω] とする。 | 100 | 102 | 103 | 104 | The voltage between b - b' is, 100 + 0.1 × 5 × 2 = 101 [V] The voltage between a - a' is, 101+0.1 × (10+5) × 2 = 104 [V] | 2013_1,
7 | In a single-phase three-wire circuit as shown in the figure, what is the smallest value indicated by the ammeter (A in the circle)? However, H in the circle is an electric heater with a rated voltage of 100 [V]. | Picture_7 | When switches a and b are closed. | When switches c and d are closed. | When switches a and d are closed. | When switches a, b, and d are closed. | 3 | ['場合(ばあい)- Case', '定格(ていかく)- Rated value', '電圧(でんあつ)- Voltage', '定格(ていかく)- Rated value'] | {図}のような{単相} 3 {線}式{回路}で{電流}計（丸の中にA）の{指示}{値}が最も小さいものは。ただし，丸の中に H は{定格}{電圧} 100 [V] の{電熱器}である。 | {スイッチ}a，bを閉じた{場合}。 | {スイッチ}c，dを閉じた{場合}。 | {スイッチ}a，dを閉じた{場合}。 | {スイッチ}a，b，dを閉じた{場合}。 |  | 2013_1,
8 | What is the allowable current [A] per wire when five 600 V vinyl insulated wires (annealed copper wires) with a diameter of 1.6 [mm] are installed in a low-voltage indoor wiring work using metal pipes? However, the ambient temperature shall be 30 [°C] or less, and the current phenomenon coefficient shall be 0.56. |  | 15 | 17 | 19 | 27 | 1 | ['電流(でんりゅう)- Electric current', '電線(でんせん)- Electric cable', '直径(ちょっけい)- Diameter', '低圧(ていあつ)- Low voltage'] | {金属}管による{低圧}{屋内配線}{工事}で，{管内}に{直径} 1.6 [mm] の 600 V ビニル{絶縁}{電線}（軟{銅線}） 5 本を収めて{施設}した{場合}，{電線} 1 本{当たり}の{許容}{電流} [A] は。ただし，{周囲}{温度}は 30 [°C] {以下}，{電流}現象{係数}は 0.56 とする。 | 15 | 17 | 19 | 27 | Allowable current for insulated wire (single wire) is 27 [A] 27 × 0.56 = 15.12 [A] | 2013_1,
9 | If simple contact protection measures are not applied to low-voltage equipment (there is a risk of human beings touching it easily), is it possible to omit the installation of an earth leakage breaker in the circuit that supplies electricity to it? |  | An outdoor unit of a 100 [V] room air conditioner was installed in a wet place, and the grounding resistance of the metal outer case was 100 [Ω]. | A 100 [V] electric washing machine was installed in a wet place, and the ground resistance value of the metal outer case was 80 [Ω]. | Equipment with a double-insulated structure, which is subject to the Electrical Appliance and Material Safety Law, was installed outdoors. | A 200 [V] three-phase induction motor was installed in a damp place in a factory, and the ground resistance value of the iron stand was 10 [Ω]. | 3 | ['構造(こうぞう)- Structure', '外箱(そとばこ)- Outer case', '金属製(きんぞくせい)- Made of metal', '電気(でんき)- Electricity', '防護(ぼうご)- Protection', '機械(きかい)- Machine', '低圧(ていあつ)- Low voltage'] | {低圧}の{機械}{器具}に{簡易}{接触}{防護}{措置}を施してない（人が{容易}に触れるおそれがある）{場合}，それに{電気}を供給する{電路}に{漏電}{遮断器}の取り付けが{省略}できるものは。 | 100 [V] ルームエアコンの{屋外}機を{水気}のある{場所}に{施設}し，その{金属}製{外箱}の{接地}抵抗が 100 [Ω] であった。 | 100 [V] の{電気}洗濯機を{水気}のある{場所}に{設置}し，その{金属}製{外箱}の{接地}抵抗{値}が 80 [Ω] であった。 | {電気}{用品}安全法の{適用}を受ける二重{絶縁}{構造}の{機械}{器具}を{屋外}に{施設}した。 | {工場}で 200 [V] の{三相}{誘導電動機}を{湿気}のある{場所}に{施設}し，その鉄台の{接地}抵抗{値}が 10 [Ω] であった。 |  | 2013_1,
10 | What is an appropriate combination of the thickness of the branch circuit wire (annealed copper wire) protected by the circuit breaker with a rated current of 30 [A] and the graphical symbol of the outlet that can be connected? However, outlets shall not be dual-use outlets. |  | Picture_10_A | Picture_10_B | Picture_10_C | Picture_10_D | 3 | ['記号(きごう)- Symbol', '兼用(けんよう)- Multi-use', '接続(せつぞく)- Connection', '分岐(ぶんき)- Divergence', '定格(ていかく)- Rated value'] | {定格}{電流} 30 [A] の{配線}用{遮断器}で保護される{分岐}{回路}の{電線}（軟{銅線}）の太さと，{接続}できる{コンセント}の{図}{記号}の{組合せ}として，{適切}なものは。ただし，{コンセント}は{兼用}{コンセント}ではないものとする。 | Picture_10_A | Picture_10_B | Picture_10_C | Picture_10_D |  | 2013_1,
11 | What is an appropriate combination of the type of electrical work and the tools used in that work? |  | Metal pipe work and reaming | Synthetic resin pipework and pipe benders | Metal wire work and bolt clipper | Bus duct work and crimping pliers | 1 | ['圧着(あっちゃく)- Crimping', '種類(しゅるい)- Variety', '電気工事(でんきこうじ)-Electrical work '] | {電気}{工事}の{種類}と，その{工事}で{使用}する{工具}の{組合せ}として，{適切}なものは。 | {金属}{管}{工事}とリーマ | {合成}樹脂{管}{工事}とパイプベンダ | {金属}{線}ぴ{工事}とボルトクリッパ | バスダクト{工事}と{圧着}ペンチ |  | 2013_1,
12 | What is the maximum permissible temperature [°C] for the insulation of 600 V vinyl insulated wires (IV) used as low-voltage indoor wiring? |  | 30 | 45 | 60 | 75 | 3 | ['圧着(あっちゃく)- Crimping', '種類(しゅるい)- Variety', '電気工事(でんきこうじ)- Electrical work'] | {低圧}{屋内配線}として{使用}する 600 V ビニル{絶縁}{電線}（IV）の{絶縁}{物の}最高{許容}{温度} [°C] は。 | 30 | 45 | 60 | 75 |  | 2013_1,
13 | Which of the following descriptions about low-voltage three-phase squirrel-cage induction motors for general use is incorrect? |  | The starting current for a direct-on-line (full voltage) start is about 4 to 8 times the full load current. | Rotational speed increases when the frequency of the power supply changes from 60 [Hz] to 50 [Hz]. | As the load increases, the rotation speed decreases slightly. | Reversing any two of the three connections will reverse the rotation. | 2 | ['電流(でんりゅう)- Electric current', '始動(しどう)- Starting', '記述(きじゅつ)- Description', '低圧(ていあつ)- Low voltage'] | 一般用{低圧}{三相}かご形{誘導電動機}に関する{記述}で，誤っているものは。 | じか入れ（全{電圧}）{始動}での{始動}{電流}は全{負荷}{電流}の 4 ～ 8 倍{程度}である。 | {電源}の{周波数}が 60 [Hz] から 50 [Hz] に変わると{回転}{速度}が{増加}する。 | {負荷}が{増加}すると{回転}{速度}がやや低下する。 | 3本の結{線}のうちいずれか 2 本を入れ替えると逆{回転}する。 |  | 2013_1,
14 | Compared to fluorescent lamps that use a starter tube, what are the characteristics of fluorescent lamps dedicated to high-frequency lighting that are incorrect? |  | Less flicker. | High luminous efficiency. | Inverter is used. | It takes a long time to light up. | 4 | ['点灯(てんとう)- Turning on a light', '蛍光灯(けいこうとう)- Fluorescent lamp'] | {点灯}{管}を用いる{蛍光灯}と{比較}して，{高周波}{点灯}{専用}形の{蛍光灯}の特徴として，誤っているものは。 | ちらつきが少ない。 | 発光効率が{高い}。 | インバータが{使用}されている。 | {点灯}に要する時間が長い。 |  | 2013_1,
15 | What is the name of the part circled in the equipment shown in the photo? | Picture_15 | Electromagnetic contactor | Earth leakage circuit breaker | Thermal Power Appliances | Leakage alarm | 1 | ['漏電(ろうでん)- Leakage', '部分(ぶぶん)- Portion', '写真(しゃしん)- Photography'] | {写真}に{示す}{器具}の○で囲まれた{部分}の{名称}は。 | {電磁}{接触}器 | {漏電}{遮断器} | 熱動継電器 | {漏電}{警報器} |  | 2013_1,
16 | What is the name of the measuring instrument shown in the photo? | Picture_16 | Circuit meter | Frequency meter | Earth resistance meter | Illuminometer | 4 | ['回路計(かいろけい)- Multimeter', '測定器(そくていき)- Measuring instrument'] | {写真}に{示す}{測定}器の{名称}は。 | {回路}計 | {周波数}計 | {接地}抵抗計 | {照度}計 |  | 2013_1,
17 | What is the use of the equipment shown in the photo? | Picture_17 | Used as a wiring device in a humid place such as under the floor. | It is used when lighting fixtures, etc. are used at arbitrary positions in shops, etc. | Used for floor duct and distribution board connection equipment. | It is used as a wiring material for large-capacity main lines. | 2 | ['分電盤(ぶんでんばん)- Distribution board', '接続(せつぞく)- Connection', '配線(はいせん)- Wiring', '用途(ようと)- Use'] | {写真}に{示す}{器具}の{用途}は。 | {床}下等{湿気}の多い{場所}の{配線}{器具}として用いる。 | {店舗}などで照明{器具}等を任意の{位置}で{使用}する{場合}に用いる。 | フロアダクトと{分電盤}の{接続}{器具}に用いる。 | {容量}の{大きな}{幹線}用{配線}{材料}として用いる。 |  | 2013_1,
18 | What is the use of the equipment shown in the photo? | Picture_18 | Used to adjust the brightness of an incandescent lamp. | Used for automatic flashing when a person approaches. | Used to improve the power factor of fluorescent lamps. | It is used to automatically flash outdoor lights etc. according to the brightness of the surroundings. | 4 | ['周囲(しゅうい)- Surroundings', '自動(じどう)- Automatic', '電灯(でんとう)- Electric light'] | {写真}に{示す}{器具}の{用途}は。 | 白熱{電灯}の明るさを調節するのに用いる。 | 人の{接近}による{自動}点滅に用いる。 | {蛍光灯}の{力率}改善に用いる。 | {周囲}の明るさに応じて{屋外}灯などを{自動}点滅させるのに用いる。 |  | 2013_1,
19 | What is inappropriate for low-voltage indoor wiring work with a working voltage of 100 [V]? |  | During the cable construction, the vinyl sheathed cable and the gas pipe were installed so that they would not come into contact with each other. | In the floor duct work, he omitted the D-class grounding work because the length of the duct was short. | In the metal pipe work, the wire lath at the penetration point of the wire lath was sufficiently cut open, and the metal pipe in the penetration part was put into the synthetic resin pipe. | In the synthetic resin pipe work, the distance between the support points of the pipe was set to 1.5 [m]. | 2 | ['力率(りきりつ)- Power factor', '接近(せっきん)- Getting closer', '電灯(でんとう)- Electric light'] | {使用}{電圧}100[V]の{低圧}{屋内配線}{工事}で，{不適切}なものは。 | ケーブル{工事}で，ビニル{外装}ケーブルとガス{管}が{接触}しないように{施設}した。 | フロアダクト{工事}で，ダクトの{長さ}が短いので D {種}{接地}{工事}を{省略}した。 | {金属}{管}{工事}で，ワイヤラス張りの貫通{箇所}のワイヤラスを十分に切り開き，貫通{部分}の{金属}{管}を{合成}樹脂{管}に収めた。 | {合成}樹脂{管}{工事}で，その{管}の支持点間の{距離}を 1.5 [m] とした。 |  | 2013_1,
20 | What is unsuitable for construction of neon discharge lamps where the working voltage of the indoor tube lamp circuit exceeds 1000 [V]? However, it shall have simple contact protective measures (those that are not likely to be easily touched by people). |  | The 100 [V] power supply circuit to the neon transformer was a dedicated circuit, and a 20 [A] circuit breaker was installed. | The wiring on the secondary side (tube lamp circuit) of the neon transformer was installed in a concealed place where it could not be inspected. | D-class grounding work was performed on the metal outer case of the neon transformer. | Neon wires were used for the wiring on the secondary side (tube lamp circuit) of the neon transformer. | 2 | ['金属製(きんぞくせい)- Made of metal', '点検(てんけん)- Inspection', '変圧器(へんあつき)- Transformer', '防護(ぼうご)- Protection', '放電灯(ほうでんとう)- Discharge lamp', '回路(かいろ)- Circuit', '屋内(おくない)- Indoor '] | {屋内}の{管}灯{回路}の{使用}{電圧}が 1000 [V] を超えるネオン放{電灯}の{工事}として，{不適切}なものは。ただし，{簡易}{接触}{防護}{措置}が施してあるもの（人が{容易}に触れるおそれがないもの）とする。 | ネオン{変圧器}への 100 [V] {電源}{回路}は，{専用}{回路}とし，20 [A] {配線}用{遮断器}を{設置}した。 | ネオン{変圧器}の二次側（{管}灯{回路}）の{配線}を，{点検}できない隠ぺい{場所}に{施設}した。 | ネオン{変圧器}の{金属}製{外箱}に D {種}{接地}{工事}を施した。 | ネオン{変圧器}の二次側（{管}灯{回路}）の{配線}を，ネオン{電線}を{使用}し，がいし引き{工事}により{施設}し，{電線}の支持点間の{距離}を 1 [m] とした。 |  | 2013_1,
21 | What is the correct combination of the symbol for low-voltage indoor wiring and the installation method for it? |  | A thin steel conduit with an outer diameter of 19 mm was used as an exposed wiring. | A synthetic resin flexible conduit with an inner diameter of 16 mm was used as a ceiling concealed wiring. | It was constructed as an exposed wiring with a hard vinyl chloride conduit tube with an inner diameter of 16 mm. | It was constructed as a ceiling concealed wiring with a steel conduit (screwless conduit) with an outer diameter of 19 mm. | 2 | ['天井(てんじょう)- Ceiling', '配線(はいせん)- Wiring', '記号(きごう)- Symbol'] | {低圧}{屋内配線}の{図}{記号}と、それに対する{施工}{方法}の{組合せ}として、{正しい}ものは。 | Figure_21_A#{外径}19 [mm] の薄鋼{電線}{管}で露出{配線}として{工事}した。 | Figure_21_B#{外径}19 [mm] の薄鋼{電線}{管}で露出{配線}として{工事}した。 | Figure_21_C#{内径}16 [mm] の{硬質}塩化ビニル{電線}{管}で露出{配線}と して{工事}した。 | Figure_21_D#{外径}19 [mm] の{鋼製}{電線}{管} (ねじなし{電線}{管})で{天井} 隠ぺい{配線}として{工事}した。 |  | 2013_1,
22 | Indoor wiring with a working voltage of 100 [V], which is inappropriate as a type of construction work in a humid place. |  | Metal pipe work with a moisture-proof device in a concealed place where inspection is not possible | Synthetic resin pipe work with a moisture-proof device in a concealed place that cannot be inspected (excluding CD pipes) | Cable construction at the unfolded location | At the unfolded place, metal wire work | 4 | ['点検(てんけん)- Inspection', '防湿(ぼうしつ)- Damp proofing', '場所(ばしょ)- Place; location', '屋内配線(おくないはいせん)- Interior wiring', '電圧(でんあつ)- Voltage'] | {使用}{電圧}100[V]の{屋内配線}で，{湿気}の多い{場所}における{工事}の{種類}として，{不適切}なものは。 | {点検}できない隠ぺい{場所}で，{防湿}装置を施した{金属}{管}{工事} | {点検}できない隠ぺい{場所}で，{防湿}装置を施した{合成}樹脂{管}{工事}（CD{管}を除く） | 展開した{場所}で，ケーブル{工事} | 展開した{場所}で，{金属}{線}ぴ{工事} |  | 2013_1,
23 | What is an inappropriate construction method for a three-phase motor circuit with a working voltage of 200[V]? |  | Outdoor vinyl insulated wires were used for metal pipe construction. | The distance between the supporting points of the 600 V vinyl-insulated vinyl-sheathed cable attached along the construction material was 2 [m] or less. | Since the pipe length is 3 [m] and the metal pipe is installed in a dry place, the D-class grounding work for the metal pipe was omitted. | A 600 V vinyl insulated wire was used for a construction using a flexible conduit made of two types of metal. | 1 | ['工事(こうじ)- Construction work', '絶縁(ぜつえん)- Insulation', '電動機(でんどうき)- Electric motor', '電圧(でんあつ)- Voltage'] | {使用}{電圧}200[V]の{三相}{電動機}{回路}の{施工}{方法}で，{不適切}なものは。 | {金属}{管}{工事}に{屋外}用ビニル{絶縁}{電線}を{使用}した。 | 造営材に沿って取り付けた 600 V ビニル{絶縁}ビニルシースケーブルの支持点間の{距離}を 2 [m] {以下}とした。 | 乾燥した{場所}の{金属}{管}{工事}で，{管}の{長さ}が 3 [m] なので{金属}{管}の D {種}{接地}{工事}を{省略}した。 | 2{種}{金属}製可とう{電線}{管}を用いた{工事}に 600 V ビニル{絶縁}{電線}を{使用}した。 |  | 2013_1,
24 | What is the correct combination of measuring instruments used in low-voltage circuits and their applications? |  | Checking the presence or absence of charge in the voltage detector and circuit | Measurement of rotation speed of phase detector and motor | Circuit meter and insulation resistance measurement | Confirmation of phase sequence (phase rotation) of tachometer and three-phase circuit | 1 | ['充電(じゅうでん)- Charging', '電動機(でんどうき)- Electric motor', '検電器(けんでんき)- Voltage detector', '測定器(そくていき)- Measuring instrument'] | {低圧}{電路}で{使用}する{測定}器とその{用途}の{組合せ}として，{正しい}ものは。 | {検電器}と{電路}の{充電}の有無の{確認} | 検相器と{電動機}の{回転}{速度}の{測定} | {回路}計と{絶縁}抵抗の{測定} | {回転}計と{三相}{回路}の相順（相{回転}）の{確認} |  | 2013_1,
25 | When measuring earth resistance using a direct-reading earth resistance meter, what is the most appropriate arrangement of two auxiliary earth electrodes P (for voltage) and C (for current) with respect to the earth electrode E to be measured? |  | Picture_25_A | Picture_25_B | Picture_25_C | Picture_25_D | 4 | ['接地(せっち)- Ground (electricity)', '配置(はいち)- Layout', '抵抗(ていこう)- Resistance'] | 直読式{接地}抵抗計を用いて，{接地}抵抗を{測定}する{場合}，被{測定}{接地}{極} E に対する，2 つの{補助}{接地}{極} P （{電圧}用）及び C （{電流}用）の{配置}として，最も{適切}なものは。 | Picture_25_A | Picture_25_B | Picture_25_C | Picture_25_D |  | 2013_1,
26 | In single-phase three-wire 100 / 200 V indoor wiring, the minimum value of insulation resistance for each circuit that can be separated by a switch or overcurrent circuit breaker is specified in the "Ministerial Ordinance for Establishing Technical Standards for Electrical Equipment". Which combination of values ​​[MΩ] is correct? |  | Between the circuit and the earth 0.2, between the wires 0.4 | 0.2 between the circuit and the earth, 0.2 between the wires | Between the circuit and the earth 0.1, between the wires 0.2 | 0.1 between the circuit and the earth, 0.1 between the wires | 4 | ['電線(でんせん)- Electric cable', '電路(でんろ)- Electrical circuit', '遮断器(しゃだんき)- Circuit breaker', '開閉器(かいへいき)- Switch', '屋内配線(おくないはいせん)- Interior wiring', '単相(たんそう)- Single phase'] | {単相} 3 線式 100 / 200 V の{屋内配線}において，{開閉器}又は過{電流}{遮断器}で区切ることができる{電路}ごとの{絶縁}抵抗の{最小}{値}として，「{電気}{設備}に関する{技術基準}を定める{省令}」に規定されている{値} [MΩ] の{組合せ}で，{正しい}ものは。 | {電路}と{大地}間 0.2，{電線}{相互}間 0.4 | {電路}と{大地}間 0.2，{電線}{相互}間 0.2 | {電路}と{大地}間 0.1，{電線}{相互}間 0.2 | {電路}と{大地}間 0.1，{電線}{相互}間 0.1 |  | 2013_1,
27 | Because it was difficult to measure the insulation resistance in a circuit with a low working voltage, we checked the insulation performance by measuring the leakage current when the working voltage was applied. What is the maximum value [mA] of leakage current that can be judged to have the insulation performance specified in "Interpretation of Technical Standards for Electrical Equipment"? |  | 0.1 | 0.2 | 1 | 2 | 3 | ['最大値(さいだいち)- Global maximum', '電気設備(でんきせつび)- Electrical equipment', '状態(じょうたい)- State', '測定(そくてい)- Measurement', '電路(でんろ)- Electrical circuit', '電圧(でんあつ)- Voltage'] | {使用}{電圧}が{低圧}の{電路}において，{絶縁}抵抗{測定}が困難であったため，{使用}{電圧}が加わった{状態}で漏えい{電流}により{絶縁}{性能}を{確認}した。「{電気}{設備}の{技術基準}の{解釈}」に定める{絶縁}{性能}を有していると{判断}できる漏えい{電流}の{最大値} [mA] は。 | 0.1 | 0.2 | 1 | 2 |  | 2013_1,
28 | What are the incorrect statements regarding the duties or limitations of electricians? |  | An electrician must carry an electrician's license when engaging in electrical work as stipulated by the Electrician Law. | With a second-class electrician license only, you can engage in all electrical work for low-voltage parts of private electric facilities with a maximum power of less than 500 [kW] for demand equipment. | When an electrician changes his/her name, he/she must apply to the prefectural governor who issued the license to rewrite the license. | When performing electrical work as stipulated by the Electrician Law, an electrician must perform the work in compliance with the ministerial ordinance that establishes technical standards for electrical equipment. | 2 | ['低圧(ていあつ)- Low voltage', '作物(さくもつ)- Crops; (agricultural) produce', '免状(めんじょう)- Diploma', '制限(せいげん)- Restriction', '義務(ぎむ)- Duty'] | {電気}{工事}士の{義務}又は{制限}に関する{記述}として，誤っているものは。 | {電気}{工事}士は，{電気}{工事}士法で定められた{電気}{工事}の{作業}に{従事}するときは，{電気}{工事}士{免状}を携帯していなければならない。 | 第二{種}{電気}{工事}士のみの{免状}で，{需要}{設備}の最大{電力}が 500 [kW] 未満の自{家用}{電気}工{作物}の{低圧}{部分}の{電気}{工事}のすべての{作業}に{従事}することができる。 | {電気}{工事}士は，氏名を変更したときは，{免状}を交付した都{道}府県知事に申請して{免状}の書換えをしてもらわなければならない。 | {電気}{工事}士は，{電気}{工事}士法で定められた{電気}{工事}の{作業}を行うときは，{電気}{設備}に関する{技術基準}を定める{省令}に適合するよう{作業}を行わなければならない。 |  | 2013_1,
29 | Under the Electrical Appliance and Material Safety Law, what are the specified electrical appliances and materials? |  | Metal conduit tube with an outer diameter of 25 [mm] | Synthetic resin insulated wire with nominal cross-sectional area of ​​150 [mm²] | Cable wiring switch box | Circuit breaker for wiring with a rated current of 60 [A] | 4 | ['電流(でんりゅう)- Electric current', '用品(ようひん)- Articles', '電気(でんき)- Electricity', '特定(とくてい)- Specific'] | {電気}{用品}安全法において，{特定}{電気}{用品}の{適用}を受けるものは。 | {外径} 25 [mm] の{金属}製{電線}{管} | {公称}{断面積} 150 [mm²] の{合成}樹脂{絶縁}{電線} | ケーブル{配線}用{スイッチ}ボックス | {定格}{電流} 60 [A] の{配線}用{遮断器} |  | 2013_1,
30 | What is subject to the application of electric tools for general use. However, the power generation equipment shall be installed in one premises with a low voltage of 600 [V] or less. |  | A kindergarten equipped with solar cell power generation equipment with low-voltage power reception of 30 [kW] received power and 15 [kW] output | Movie theater equipped with emergency internal combustion power generation equipment with low-voltage power reception, power reception of 30 [kW] and output of 20 [kW] | A farm equipped with a wind power generation facility with an output of 15 [kW] electrically connected to a solar cell power generation facility with a receiving power of 30 [kW] and an output of 40 [kW] with low-voltage power reception. | High-pressure power receiving で, receiving power 50 [kW] の machine shop | 1 | ['高圧(こうあつ)- High pressure', '設備(せつび)- Equipment', '受電(じゅでん)- Receiving electricity', '構内(こうない)- Grounds', '発電(はつでん)- Electricity generation', '適用(てきよう)- Applying'] | 一般用{電気}工{作物}の{適用}を受けるものは。ただし，{発電}{設備}は{低圧} 600 [V] {以下}で，1 {構内}に{設置}するものとする。 | {低圧}{受電}で，{受電}{電力} 30 [kW]，{出力} 15 [kW] の太陽{電池}{発電}{設備}を備えた幼稚園 | {低圧}{受電}で，{受電}{電力} 30 [kW]，{出力} 20 [kW] の非常用内燃力{発電}{設備}を備えた{映画館} | {低圧}{受電}で，{受電}{電力} 30 [kW]，{出力} 40 [kW] の太陽{電池}{発電}{設備}と{電気}的に{接続}した{出力} 15 [kW] の風力{発電}{設備}を備えた農園 | {高圧}{受電}で，{受電}{電力} 50 [kW] の{機械}{工場} |  | 2013_1,
31 | What is the name of the graphic symbol indicated by ①? |  | Incandescent lamp | Confirmation indicator | Hot wire automatic switch | Position indicator light | 2 | ['表示灯(ひょうじとう)- Signal light', '確認(かくにん)- Confirmation', '白熱灯(はくねつとう)- Incandescent lamp'] | ①で{示す}{図}{記号}の{名称}は。 | {白熱灯} | {確認}{表示}灯 | 熱{線}式{自動}{スイッチ} | {位置}{表示}灯 |  | 2013_1,
32 | What is the permissible maximum value [Ω] of the grounding resistance in the grounding work of the part indicated by ②? |  | 10 | 100 | 300 | 500 | 4 | ['最大値(さいだいち)- Global maximum', '部分(ぶぶん)- Portion'] | ②で{示す}{部分}の{接地}{工事}における{接地}抵抗の{許容}される{最大値}[Ω]は | 10 | 100 | 300 | 500 |  | 2013_1,
33 | What is the name of the symbol shown in ③? |  | Dimmer | Clear through | Delay switch | Remote control switch | 1 | ['調光器(ちょうこうき)- Dimmer', '記号(きごう)- Symbol'] | ③で{示す}{図}{記号}の{名称}は。 | {調光器} | 素通し | {遅延}{スイッチ} | リモコン{スイッチ} |  | 2013_1,
34 | What is the minimum number of wires (number of cores) for the part indicated by ④? |  | 2 | 3 | 4 | 5 | 1 | ['最少(さいしょう)- Fewest'] | ④で{示す}{部分}の{最少}{電線}{本数}（心線数）は。 | 2 | 3 | 4 | 5 |  | 2013_1,
35 | What are the symbols (types) of wires that cannot be used in FEP (corrugated rigid synthetic resin pipe) shown in ⑤? |  | VVF | CV | IV | VVR | 3 | ['種類(しゅるい)- Variety', '硬質(こうしつ)- Hardness'] | ⑤で{示す}FEP（波付{硬質}{合成}樹脂{管}）内に{使用}できない{電線}の{記号}（{種類}）は。 | VVF | CV | IV | VVR |  | 2013_1,
36 | The part indicated by ⑥ is an automatic flasher for outdoor lights. What is the correct sidenote for the graphic symbol? |  | A | P | T | L | 1 | ['表示(ひょうじ)- Idication', '自動(じどう)- Automatic'] | ⑥で{示す}{部分}は{屋外}灯の{自動}{点滅器}である。 その{図}{記号}の傍記{表示}として、{正しい}ものは。 | A | P | T | L |  | 2013_1,
37 | What is the minimum thickness diameter [mm] of the wire (annealed copper wire) that can be used in the small force circuit shown in ⑦? |  | 0.8 | 1.2 | 1.6 | 2.0 | 1 | ['勢力(せいりょく)- Influence'] | ⑦で{示す}{部分}の小{勢力}{回路}で{使用}できる{電線}（軟{銅線}）の{最小}太さの{直径}[mm]は。 | 0.8 | 1.2 | 1.6 | 2.0 |  | 2013_1,
38 | What is the graphical symbol of the instrument attached to the part indicated by ⑧? |  | Picture_38_A | Picture_38_B | Picture_38_C | Picture_38_D | 4 | ['記号(きごう)- Symbol; code', '計器(けいき)- Meter'] | ⑧で{示す}{部分}に取り付ける{計器}の{図}{記号}は。 | Picture_38_A | Picture_38_B | Picture_38_C | Picture_38_D |  | 2013_1,
39 | What is the name of the symbol shown in ⑨? |  | Rise | Reduction | Power receiving point | Branch line | 3 | ['名称(めいしょう)- Name; title'] | ⑨で{示す}{図}{記号}の{名称}は。 | 立上り | 引下げ | {受電}点 | 支{線} |  | 2013_1,
40 | What is the meaning of the abbreviation "WP" in the graphical symbol shown in ⑩? |  | Outdoor type | Rainproof type | Hook type | Wide type | 2 | ['表示(ひょうじ)- Indication', '記号(きごう)- Symbol'] | ⑩で{示す}{図}{記号}の傍記{表示}「WP」の意味は。 | {屋外}形 | 防雨形 | 引掛形 | ワイド形 |  | 2013_1,
41 | What is the appropriate tool to use when crimping the VVF joint box shown in ⑪ with a ring sleeve E type connection? |  | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D | 2 | ['部分(ぶぶん)- Portion', '接続(せつぞく)- Connection', '圧着(あっちゃく)- Pressure bonding'] | ⑪で{示す}VVF用ジョイントボックス{部分}の{工事}を、リングスリーブE形による{圧着}{接続}で行う{場合}に用いる{工具}として、{適切}なものは。 | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D |  | 2013_1,
42 | As for the equipment with the symbol shown in ⑫. |  | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D | 4 | ['器具(きぐ)- Utensil'] | ⑫で{示す}{図}{記号}の{器具}は。 | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D |  | 2013_1,
43 | As for the equipment with the symbol shown in ⑬. However, the diagram below the photo shows the configuration of the contacts. |  | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D | 2 | ['構成(こうせい)- Composition', '接点(せってん)- Tangent point'] | ⑬で{示す}{図}{記号}の{器具}は。 ただし、{写真}下の{図}は、{接点}の{構成}を{示す}。 | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D |  | 2013_1,
44 | In the joint box in the ceiling of the part indicated by ⑭, if all the connections are crimp connections, what is the appropriate combination of the type and minimum number of ring sleeves to be used? However, the wires to be used shall be VVF1.6-2C, and all wires passing through the joint box shall have connection points. |  | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D | 1 | ['種類(しゅるい)- Variety', '接続(せつぞく)- Connection'] | ⑭で{示す}{部分}の{天井}内のジョイントボックス内において、{接続}をすべて{圧着}{接続}とする{場合}、{使用}するリングスリーブの{種類}と{最少}{個数}の{組合せ}で、{適切}なものは。 ただし、{使用}する{電線}はVVF1.6-2Cとし、ジョイントボックスを経由する{電線}は、すべて{接続}{箇所}を設けるものとする。 | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D |  | 2013_1,
45 | If all the connections in the joint box for VVF shown in ⑮ are plug-in connectors, what is the appropriate combination of plug-in connector type and minimum number to be used? However, the wires to be used shall be VVF1.6-2C, and all wires passing through the joint box shall have connection points. |  | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D | 3 | ['種類(しゅるい)- Variety', '場合(ばあい)- Case; situation', '接続(せつぞく)- Connection'] | ⑮で{示す}VVF用ジョイントボックス内の{接続}をすべて差込形{コネクタ}とする{場合}、{使用}する差込形{コネクタ}の{種類}と{最少}{個数}の{組合せ}で、{適切}なものは。 ただし、{使用}する{電線}はVVF1.6-2Cとし、ジョイントボックスを経由する{電線}は、すべて{接続}{箇所}を設けるものとする。 | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D |  | 2013_1,
46 | The equipment to be attached to the part indicated by ⑯. |  | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D | 3 | ['器具(きぐ)- Utensil', '部分(ぶぶん)- Portion'] | ⑯で{示す}{部分}に取り付ける{器具}は。 | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D |  | 2013_1,
47 | What measures the load current of the part indicated by ⑰? |  | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D | 4 | ['負荷(ふか)- Load', '電流(でんりゅう)- Electric current'] | ⑰で{示す}{部分}の{負荷}{電流}を{測定}するものは。 | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D |  | 2013_1,
48 | ⑱ As for the equipment with the graphical symbol. |  | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D | 4 | ['記号(きごう)- Symbol'] | ⑱で{示す}{図}{記号}の{器具}は。 | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D |  | 2013_1,
49 | What is not generally used in the construction of the 3rd floor plan? |  | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D | 2 | ['施工(せこう)- Construction', '平面図(へいめんず)- Ground plan'] | 3階{平面図}の{施工}で、{一般的}に{使用}されることのないものは。 | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D |  | 2013_1,
50 | What is the appropriate combination of the shape of the plate used for the third floor and the minimum number of plates? |  | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D | 1 | ['適切(てきせつ)- Appropriate', '最少(さいしょう)- Fewest', '形状(けいじょう)- Shape'] | 3階{部分}に{使用}するプレートの{形状}とその{最少}枚数の{組合せ}で、{適切}なものは。 | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D |  | 2013_1,