## Sheet1
no | Eng | Picture | Option_1_Eng | Option_2_Eng | Option_3_Eng | Option_4_Eng | Ans | Vocab | Jpn | Option_1_Jpn | Option_2_Jpn | Option_3_Jpn | Option_4_Jpn | Exp | comment
1 | In the circuit shown in the figure, when the switch S is closed, the voltage [V] between terminals a and b is: | Picture_1 | 30 | 40 | 50 | 60 | 4 | ['電圧(でんあつ)- Voltage', '回路(かいろ)- Circuit'] | {図}のような{回路}で、{スイッチ}Sを閉じたとき、a-b {端子}間の{電圧}〔V〕は。 | 30 | 40 | 50 | 60 | R1 + R2 = 50 + 50 = 100 Ω I = V/R = 120/100 = 1.2A V=IR=1.2×50=60V | 2019_1, 2015_2,
2 | When 100V, 50Hz AC voltage was applied to the coil, a current of 6A flowed. What is the current [A] that flows when a 100V, 60Hz AC voltage is applied to this coil? However, the resistance of the coil is assumed to be negligible. |  | 4 | 5 | 6 | 7 | 2 | ['抵抗(ていこう)- Resistance', '電流(でんりゅう)- Electric current', '電圧(でんあつ)- Voltage', '交流(こうりゅう)- Exchange'] | {コイル}に100V、50Hzの{交流}{電圧}を加えたら6Aの{電流}が流れた。この{コイル}に100V、60Hzの{交流}{電圧}を加えたときに{流れる}{電流}〔A〕は。 ただし、{コイル}の抵抗は無視できるものとする。 | 4 | 5 | 6 | 7 | I = 6A x 1/60Hz/50Hz = 6 x 50/60 = 5A. | 2018_1, 2015_2,
3 | What is the formula for the electrical resistance [Ω] of a conductor with resistivity ρ [Ω・m], diameter D [mm], and length L [m]? |  | Picture_3_A | Picture_3_B | Picture_3_C | Picture_3_D | 1 | ['導線(どうせん)- Conducting wire', '長さ(なが)- Length', '直径(ちょっけい)- Diameter'] | {抵抗率}ρ〔Ω・m〕、{直径}D〔mm〕、{長さ}L〔m〕の{導線}の{電気}抵抗〔Ω〕を表す式は。 | Picture_3_A | Picture_3_B | Picture_3_C | Picture_3_D |  | 2015_2, 2017_2,
4 | What is the amount of electric power [kW・h] required to raise the temperature of 60 kg of water by 20 K with an electric heater? However, the specific heat of water is assumed to be 4.2 kJ/(kg K) and the thermal efficiency is assumed to be 100%. |  | 1 | 1.2 | 1.4 | 1.6 | 3 | ['熱効率(ねつこうりつ)- Thermal efficiency', '比熱(ひねつ)- Specific heat', '温度(おんど)- Temperature'] | {電熱器}により、60kgの水の{温度}を20K上昇させるのに{必要}な{電力}量〔kW・h〕は。 ただし、水の{比熱}は4.2kJ/（kg・K）とし、{熱効率}は100％とする。 | 1 | 1.2 | 1.4 | 1.6 | H = 4.2 x 60 x 20 = 5040 [kJ] 1 [kw・h] is 3600 [kJ] So, Power = H/3600=5040/3600=1.4 [kw・h] | 2019_1, 2018_2, 2015_2,
5 | What is the current I [A] flowing in a three-phase three-wire circuit as shown in the figure? |  | 8.3 | 11.6 | 14.3 | 20 | 2 | ['電流(でんりゅう)- Electric current', '回路(かいろ)- Circuit', '三相(さんそう)- Three phases'] | {図}のような{三相}3{線}式{回路}に{流れる}{電流}I［A］は。 | 8.3 | 11.6 | 14.3 | 20 | I=V/R=√3/10=20/1.73=11.6 | 2019_2, 2018_2, 2015_2,
6 | In the single-phase two-wire circuit shown in the figure, when the voltage between c and c' is 99V, the voltage between a and a' [V] is: However, r is the wire resistance [Ω]. | Picture_6 | 102 | 103 | 104 | 105 | 4 | ['抵抗(ていこう)- Resistance', '電線(でんせん)- Cable', '電圧(でんあつ)- Voltage'] | {図}のような{単相}2線式{回路}で、c-c’間の{電圧}が99Vのとき、a-a’間の{電圧}〔V〕は。 ただし、rは{電線}の抵抗［Ω］とする。 | 102 | 103 | 104 | 105 | The upper and lower rows will have the same value. So, ab is 20 x 0.1 = 2V, bc is 10 x 0.1 = 1V 2+1+99+1+2 = 105V. | 2015_2,
7 | In the single-phase three-wire circuit shown in the figure, when the resistance of each wire is 0.1Ω and the current flowing through the resistive load is 20A, the power loss [W] of this wire line is: | Picture_7 | 40 | 69 | 80 | 120 | 3 | ['電力損失(でんりょくそんしつ)- Electric power loss', '電流(でんりゅう)- Electric current'] | {図}のような{単相}3線式{回路}で、{電線}1線{当たり}の抵抗が0.1Ω、抵抗{負荷}に{流れる}{電流}がともに20Aのとき、この{電線}路の{電力}損失〔W〕は。 | 40 | 69 | 80 | 120 | P=I^2r+I^2r . P＝(20^2×0.1)+(20^2×0.1)=40+40 =80【W】 | 2015_2,
8 | What is the allowable current [A] per wire when five 600V vinyl insulated wires (annealed copper wire) with a diameter of 2.0mm are installed in the pipe for low-voltage indoor wiring work using metal pipes? However, the ambient temperature should be 30°C or less, and the current reduction factor should be 0.56. |  | 15 | 19 | 27 | 35 | 2 | ['許容(きょよう)- Permission', '銅線(どうせん)- Copper wire', '直径(ちょっけい)- Diameter', '低圧(ていあつ)- Low Voltage'] | {金属}管による{低圧}{屋内配線}{工事}で、{管内}に{直径}2.0mmの600Vビニル{絶縁}{電線}（軟{銅線}）5本を収めて{施設}した{場合}、{電線}1本{当たり}の{許容}{電流}〔A〕は。 ただし、{周囲}{温度}は30℃{以下}、{電流}{減少}{係数}は0.56とする。 | 15 | 19 | 27 | 35 | The allowable current of a diameter of 2.0mm is 35A. So, 35 x 0.56 = 19.6 | 2019_1, 2018_1, 2017_1, 2016_2, 2015_2,
9 | As shown in the figure, when branching from a low-voltage indoor main line protected by an overcurrent circuit breaker with a rated current of 60A and installing an overcurrent circuit breaker at a position of 10 m, the minimum allowable current of the wire between a and b [A] teeth. | Picture_9 | 15 | 21 | 27 | 33 | 4 | ['屋内(おくない)- Indoor ', '遮断器(しゃだんき)- Circuit breaker', '過電流(かでんりゅう)- Over current', '定格(ていかく)- Rated value'] | {図}のように{定格}{電流}60Aの過{電流}{遮断器}で保護された{低圧}{屋内}{幹線}から{分岐}して、10mの{位置}に過{電流}{遮断器}を{施設}するとき、a-b間の{電線}の{許容}{電流}の{最小}{値}〔A〕は。 | 15 | 21 | 27 | 33 | The rated current of the overcurrent circuit breaker must be 55% or more, so 60 x 0.55 = 33A. | 2019_2, 2019_1, 2018_1, 2018_2, 2016_2, 2016_1, 2015_1, 2015_2,
10 | In the design of branch circuits for low-voltage indoor wiring, what is the appropriate combination of circuit breakers, branch circuit wire thicknesses, and outlets? However, the distance from the branch point to the circuit breaker for wiring is 3m, and the distance from the circuit breaker for wiring to the outlet is 8m. Also, the outlet shall not be a dual-purpose outlet. |  | Picture_10_A | Picture_10_B | Picture_10_C | Picture_10_D | 2 | ['太い(ふと)- Fat; thick', '兼用(けんよう)- Multi-use', '分岐点(ぶんきてん)- Junction', '回路(かいろ)- Circuit'] | {低圧}{屋内配線}の{分岐}{回路}の{設計}で、配線用{遮断器}、{分岐}{回路}の{電線}の太さ及び{コンセント}の{組合せ}として、{適切}なものは。 ただし、{分岐}点から配線用{遮断器}までは3m、配線用{遮断器}から{コンセント}までは8mとし、{電線}の{数値}は{分岐}{回路}の{電線}（軟{銅線}）の太さを{示す}。また、{コンセント}は{兼用}{コンセント}ではないものとする。 | Picture_10_A | Picture_10_B | Picture_10_C | Picture_10_D |  | 2019_2, 2017_2, 2016_2, 2016_1, 2015_2, 2015_1,
11 | When a current of 25 A continuously flows through a circuit breaker with a rated current of 20 A used in a low-voltage circuit, the limit of time [minutes] within which the circuit breaker must operate automatically (maximum time) )teeth. |  | 20 | 30 | 60 | 120 | 3 | ['最大(さいだい)- Biggest', '限度(げんど)- Limit', '継続(けいぞく)- Continuation', '定格(ていかく)- Rated value'] | {低圧}{電路}に{使用}する{定格}{電流}が20Aの{配線}用{遮断器}に25Aの{電流}が{継続}して流れたとき、この{配線}用{遮断器}が{自動}的に動作しなければならない時間〔分〕の{限度}（最大の時間）は。 | 20 | 30 | 60 | 120 |  | 2015_2, 2018_1,
12 | What is the appropriate use for the knockout puncher? |  | Used to bend thick electrical conduits. | Used to make holes in metal cabinets. | Used to make holes in concrete walls. | Used for crimping thick wires. | 2 | ['圧着(あっちゃく)- Crimping', '電線(でんせん)- Electric cable', '金属製(きんぞくせい)- Made of metal'] | ノックアウトパンチャの{用途}で、{適切}なものは。 | {太い}{電線}{管}を曲げるのに用いる。 | {金属}製キャビネットに穴を開けるのに用いる。 | コンクリート{壁}に穴を開けるのに用いる。 | {太い}{電線}を{圧着}{接続}する{場合}に用いる。 |  | 2019_2, 2015_2,
13 | What is the synchronous speed [min-1] of the rotating magnetic field in a low-voltage three-phase squirrel-cage induction motor with a rated frequency of 60 Hz and four poles? |  | 1200 | 1500 | 1800 | 3000 | 3 | ['速度(そくど)- Velocity', '回転(かいてん)- Rotation', '低圧(ていあつ)- Low voltage', '周波数(しゅうはすう)- Frequency'] | {定格}{周波数}60Hz、{極}数4の{低圧}{三相}かご形{誘導電動機}における{回転}磁界の{同期}{速度}〔min-1〕は。 | 1200 | 1500 | 1800 | 3000 |  | 2015_2,
14 | Which is correct when comparing a fluorescent lamp with an incandescent lamp with the same power consumption? |  | Good power factor. | Low noise (electromagnetic noise). | Life is short. | High luminous efficiency (low power consumption at the same brightness) | 4 | ['電灯(でんとう)- Electric light', '蛍光灯(けいこうとう)- Fluorescent lamp'] | {蛍光灯}を、{同じ}消費{電力}の白熱{電灯}と比べた{場合}、{正しい}ものは。 | {力率}が良い。 | 雑音（{電磁}雑音）が少ない。 | 寿命が短い。 | 発光効率が{高い}（{同じ}明るさでは消費{電力}が少ない） |  | 2015_2,
15 | The electrical machine with the best power factor. |  | Electric toaster | Electric washing machine | Electric refrigerator | Bulb-shaped LED lamp (with built-in controller) | 1 | ['制御装置(せいぎょそうち)- Control unit', '電気機械(でんききかい)- Electric machine', '力率(りきりつ)- Power factor'] | {力率}の最も良い{電気}{機械}{器具}は。 | {電気}トースター | {電気}洗濯機 | {電気}冷蔵庫 | {電球}形LEDランプ（制御装置内蔵形） |  | 2015_2,
16 | What is the purpose of the measuring instrument shown in the photo? | Picture_16 | Used to measure earth resistance. | Used to measure insulation resistance. | Used to measure the voltage of electric circuits. | Used for frequency measurement. | 1 | ['電圧(でんあつ)- Voltage', '接地(せっち)- Ground (electricity)', '測定器(そくていき)- Measuring instrument '] | {写真}に{示す}{測定}器の{用途}は。 | {接地}抵抗の{測定}に用いる。 | {絶縁}抵抗の{測定}に用いる。 | {電気}{回路}の{電圧}の{測定}に用いる。 | {周波数}の{測定}に用いる。 |  | 2015_2,
17 | What is the purpose of the tool shown in the photo? | Picture_17 | Used to bend thick wires. | Used to prevent slippage, such as rotation of electrical conduits during construction. | Used as a branch line for electric wires. | Used to adjust the slack of the overhead wire. | 4 | ['調整(ちょうせい)- Adjustment', '画像(がぞう)- Image', '工具(こうぐ)- Hand tool'] | {写真}に{示す}{工具}の{用途}は。 | {太い}{電線}を曲げてくせをつけるのに用いる。 | {施工}時の{電線}{管}の{回転}等すベり止めに用いる。 | {電線}の支線として用いる。 | 架空{線}のたるみを調整するのに用いる |  | 2015_2,
18 | What is the name of the material shown in the photo? On the surface of the material, "Taishigaisen EM 600V EEF/F 1.6mm JIS JET <PS> E ◯◯ company TAINEN 2014" is written. | Picture_18 | Inorganic insulated cable | 600V vinyl insulated vinyl sheathed cable flat | 600V cross-linked polyethylene insulated vinyl sheathed cable | 600V polyethylene insulated flame-resistant polyethylene sheathed cable flat | 4 | ['耐燃性(たいねんせい)- Flame resistance', '絶縁(ぜつえん)- Insulation', '表面(ひょうめん)- Surface; face', '材料(ざいりょう)- Materials'] | {写真}に{示す}{材料}の{名称}は。 なお、{材料}の表面には「タイシガイセン EM 600V EEF/F 1.6mm JIS JET ＜PS＞E ◯◯社タイネン 2014」が記されている。 | 無機{絶縁}ケーブル | 600Vビニル{絶縁}ビニルシースケーブル平形 | 600V{架橋}ポリエチレン{絶縁}ビニルシースケーブル | 600Vポリエチレン{絶縁}{耐燃性}ポリエチレンシースケーブル平形 |  | 2018_2, 2015_2,
19 | In low-voltage indoor wiring work using 600V vinyl-insulated vinyl-sheathed flat cables of 1.6 mm, what is inappropriate for the insulation treatment of the end connections between insulated wires? However, the vinyl tape shall be an insulating tape with a thickness of about 0.2mm specified by JIS. |  | Connected with a ring sleeve (E type) and wrapped with vinyl tape 3 times (6 layers) over half the width of the joint. | Connected with a ring sleeve (E type), and wrapped three times (6 layers) with black adhesive polyethylene insulation tape (thickness: about 0.5 mm) over half the width of the connection. | Connected with a ring sleeve (E type), and wrapped once (2 layers) with self-adhesive insulating tape (thickness: about 0.5 mm) over half the width. | Connection was made with a plug-in connector, and the connecting part was not wrapped with vinyl tape. | 3 | ['部分(ぶぶん)- Portion', '終端(しゅうたん)- Terminus', '低圧(ていあつ)- Low voltage', '絶縁(ぜつえん)- Insulation'] | 600Vビニル{絶縁}ビニルシースケーブル平形1.6mmを{使用}した{低圧}{屋内配線}{工事}で、{絶縁}{電線}{相互}の{終端}{接続}{部分}の{絶縁}処理として、{不適切}なものは。 ただし、ビニルテープはJISに定める{厚さ}約0.2mmの{絶縁}テープとする。 | リングスリーブ（E形）により{接続}し、{接続}{部分}をビニルテープで{半幅}以上重ねて3回（6層）巻いた。 | リングスリーブ（E形）により{接続}し、{接続}{部分}を黒色粘着性ポリエチレン{絶縁}テープ（{厚さ}約0.5mm）で{半幅}以上重ねて3回（6層）巻いた。 | リングスリーブ（E形）により{接続}し、{接続}{部分}を自己融着性{絶縁}テープ（{厚さ}約0.5mm）で{半幅}以上重ねて1回（2層）巻いた。 | 差込形{コネクタ}により{接続}し、{接続}{部分}をビニルテープで卷かなかった。 |  | 2016_1, 2015_2,
20 | What is an inappropriate construction method for single-phase 3-wire 100/200V indoor wiring work in a wooden house? However, the wire to be used shall be a 600V vinyl insulated wire with a diameter of 1.6mm (annealed copper wire). |  | Two hard vinyl chloride conduits (VE) of the same diameter were connected with a TS coupling. | Wires were passed through synthetic resin flexible conduit (PF pipe) and fixed to construction materials with a distance of 1.0m between supporting points. | The metal pipe was used in a concealed place where it could not be inspected. | Synthetic resin flexible conduit (CD pipe) was laid under the wooden floor, inside the wall, and above the ceiling. | 4 | ['床下(ゆかした)- Under the floor', '直径(ちょっけい)- Diameter', '絶縁(ぜつえん)- Insulation', '工事(こうじ)- Construction work', '木造住宅(もくぞうじゅうたく)- Wooden house'] | {木造}{住宅}の{単相}3線式100/200V{屋内配線}{工事}で、{不適切}な{工事}{方法}は。 ただし、{使用}する{電線}は600Vビニル{絶縁}{電線}、{直径}1.6mm（軟{銅線}）とする。 | {同じ}径の{硬質}塩化ビニル{電線}{管}（VE）2本をTSカップリングで{接続}した。 | {合成}樹脂製可とう{電線}{管}（PF{管}）内に通線し、支持点間の{距離}を1.0mで造営材に固定した。 | {金属}{管}を{点検}できない隠ぺい{場所}で{使用}した。 | {合成}樹脂製可とう{電線}{管}（CD{管}）を{木造}の{床}下や{壁}の{内部}及び{天井}裏に配{管}した。 |  | 2019_2, 2018_2, 2015_2,
21 | Inappropriate combination of special place and low-voltage indoor wiring work to be constructed in that place. |  | Cable construction using 600V vinyl-insulated vinyl-sheathed cables protected by thick-copper conduits, where there is combustible gas, where propane gas is subdivided into other small containers. | Places with combustible dust for sifting flour, synthetic resin piping work using hard vinyl chloride conduit VE28 | Locations where hazardous materials for storing petroleum exist, metal wire construction | A place with flammable gas for spray painting work at an automobile repair shop, metal pipe work using thick steel conduit | 3 | ['塗装(とそう)- Painterwork', '危険物(きけんぶつ)- Dangerous goods', '可燃性(かねんせい)- Inflammable', '硬質(こうしつ)- Hardness', '小麦粉(こむぎこ)- Wheat flour', '場所(ばしょ)- Place', '容器(ようき)- container'] | 特殊{場所}とその{場所}に{施工}する{低圧}{屋内配線}{工事}の{組合せ}で、{不適切}なものは。 | プロパンガスを他の小さな容器に小分けする可燃性ガスのある{場所}、厚銅{電線}{管}で保護した600Vビニル{絶縁}ビニルシースケーブルを用いたケーブル{工事} | 小麦粉をふるい分けする可燃性粉じんのある{場所}、{硬質}塩化ビニル{電線}{管}VE28を{使用}した{合成}樹脂{管}{工事} | 石油を貯蔵する{危険}{物の}存在する{場所}、{金属}{線}ぴ{工事} | {自動}車修理{工場}の吹き付け塗装{作業}を行う可燃性ガスのある{場所}、厚鋼{電線}{管}を{使用}した{金属}{管}{工事} |  | 2017_1, 2015_2,
22 | For items that cannot omit Class D grounding work. However, the circuit shall be equipped with a current-operated earth leakage breaker with a rated sensitivity current of 15 mA and an operating time of 0.1 seconds or less. |  | A 3-meter-long metal tube containing power cables for three-phase 200 V (voltage to ground: 200 V) installed in a dry place. | Steel stand for a three-phase 200V (200V voltage to ground) induction motor installed on a wet concrete floor | The metal casing of a three-phase 200V (voltage to ground 200V) air compressor installed to handle on a dry wooden floor. | A 7-m-long metal tube containing wires for a single-phase, three-wire system of 100/200V (voltage to ground: 100V) installed in a dry location. | 2 | ['工事(こうじ)- Construction work', '粉塵(ふんじん)-', 'Dust', '低圧(ていあつ)- Low voltage', '特殊(とくしゅ)- Special'] | D{種}{接地}{工事}を{省略}できないものは。 ただし、{電路}には{定格}{感度}{電流} 15mA、{動作時間} 0.1秒{以下}の{電流}動作型の{漏電}{遮断器}が取り付けられているものとする。 | 乾燥した{場所}に{施設}する{三相}200V（{対地}{電圧}200V）動力{配線}の{電線}を収めた{長さ}3mの{金属}{管} | {水気}のある{場所}のコンクリートの{床}に{施設}する{三相}200V（{対地}{電圧}200V）{誘導電動機}の鉄台 | 乾燥した木製の{床}の上で取り扱うように{施設}する{三相}200V（{対地}{電圧}200V）空気{圧縮機}の{金属}製{外箱}{部分} | 乾燥した{場所}に{施設}する{単相}3線式100/200V（{対地}{電圧}100V）{配線}の{電線}を収めた{長さ}7mの{金属}{管} |  | 2019_2, 2018_1, 2015_2,
23 | Places or places where 2 cores of vinyl flat cord (cross-sectional area 0.75mm2) can be attached to 100V low-voltage indoor wiring by attaching them to insulating building materials with appropriate fasteners. |  | A place that is easily visible from the outside within a show window that is installed in a dry place and used in a dry state. | Closet walls that can be inspected without the risk of being touched by people in wooden houses | Walls of a Japanese-style room in a wooden house | Underfloor storage in kitchens used in dry conditions | 1 | ['乾燥(かんそう)- Dryness', '内部(ないぶ)- Interior', '屋内配線(おくないはいせん)- Interior wiring'] | 100Vの{低圧}{屋内配線}に、ビニル平形コード（{断面積}0.75mm2）2心を{絶縁}性のある造営材に適当な留め具で取り付けて、{施設}することができる{場所}又は{箇所}は。 | 乾燥した{場所}に{施設}し、かつ、{内部}を乾燥{状態}で{使用}するショウウインド一内の外部から見えやすい{箇所} | {木造}{住宅}の人の触れるおそれのない{点検}できる押し入れの{壁面} | {木造}{住宅}の和室の{壁面} | 乾燥{状態}で{使用}する台所の{床}下収納庫 |  | 2015_2,
24 | What is the correct wiring method for a voltmeter, ammeter, and wattmeter in a circuit from a single-phase AC power supply to a load? |  | Picture_24_A | Picture_24_B | Picture_24_C | Picture_24_D | 1 | ['結線(けっせん)- Hard wiring', '電圧計(でんあつけい)- Voltmeter', '交流電源(こうりゅうでんげん)- AC generator'] | {単相}{交流}{電源}から{負荷}に至る{回路}において、{電圧}計、{電流}計、{電力}計の結{線}{方法}として、{正しい}ものは。 | Picture_24_A | Picture_24_B | Picture_24_C | Picture_24_D |  | 2015_2,
25 | When measuring earth resistance using a direct-reading earth resistance tester, what is the most appropriate placement of the two auxiliary earth electrodes P (for voltage) and C (for current) with respect to the earth electrode E to be measured? |  | Picture_25_A | Picture_25_B | Picture_25_C | Picture_25_D | 1 | ['適切(てきせつ)- Appropriate', '配置(はいち)- Arrangement ', '場合(ばあい)- Case; situation', '抵抗(ていこう)- Resistance', '接地(せっち)- Ground (electricity)'] | 直読式{接地}抵抗計を用いて、{接地}抵抗を{測定}する{場合}、被{測定}{接地}{極}Eに対する、2つの{補助}{接地}{極}P（{電圧}用）及びC（{電流}用）の{配置}として、最も{適切}なものは。 | Picture_25_A | Picture_25_B | Picture_25_C | Picture_25_D |  | 2018_2, 2015_2,
26 | What is the correct statement about the circuit meter (tester)? |  | The digital type has a built-in battery, but the analog type does not require a battery. | We measured the resistance between the electric circuit and the ground. The measured value may be used as the insulation resistance value of the electric circuit. | When measuring AC or DC voltage, select and use the range closest to the expected value. | The output voltage at the terminals of the circuit meter when measuring resistance is an alternating voltage. | 3 | ['e電路(でんろ)- Electrical circuit', '必要(ひつよう)- Necessary', '記述(きじゅつ)- description', '測定(そくてい)- Measurement', '回路計(かいろけい)- Multimeter'] | {回路}計（テスタ）に関する{記述}として、{正しい}ものは。 | ディジタル式は{電池}を内蔵しているが、アナログ式は{電池}を{必要}としない。 | {電路}と{大地}間の抵抗{測定}を行った。その{測定}{値}は{電路}の{絶縁}抵抗{値}として{使用}してよい。 | {交流}又は{直流}{電圧}を{測定}する{場合}は、あらかじめ想定される{値}の直近上位のレンジを選定して{使用}する。 | 抵抗を{測定}する{場合}の{回路}計の{端子}における{出力}{電圧}は、{交流}{電圧}である。 |  | 2015_2,
27 | What is the correct combination of inspection items that are generally performed for inspections when low-voltage indoor wiring work for general-purpose electric facilities is completed? |  | Visual point test, absolute resistance test, ground resistance test, temperature rise test | Visual point test, continuity test, absolute resistance test, ground resistance test | Visual point test, continuity test, absolute resistance test, temperature rise test | Visual point test , Continuity test, Absolute resistance test, Absolute endurance test | 2 | ['一般的(いっぱんてき)- General', '目視(もくし)- Visual inspection', '検査(けんさ)- Inspection', '電気工(でんきこう)- Electrician'] | 一般用{電気}工{作物}の{低圧}{屋内配線}{工事}が完了したときの{検査}で、{一般的}に行われている{検査}項目の{組合せ}として、{正しい}ものは。 | 目視{点検}、{絶縁}抵抗{測定}、{接地}抵抗{測定}、{温度}上昇試験 | 目視{点検}、{導通}試験、{絶縁}抵抗{測定}、{接地}抵抗{測定} | 目視{点検}、{導通}試験、{絶縁}耐力試験、{温度}上昇試験 | 目視{点検}、{導通}試験、{絶縁}抵抗{測定}、{絶縁}耐力試験 |  | 2016_1, 2015_2,
28 | According to the Electrician Law, construction or work of electrical facilities for general use that can only be carried out by an electrician. |  | Screw the cabtyre cable to the terminal of the motor used at a voltage of 600 V or less. | Wire the secondary side of the small transformer (secondary voltage is 36V or less) used for the fire detector. | Install poles to support the wires. | Attach the switchboard to the construction material. | 4 | ['端子(たんし)- Terminal (electricity)', '電動機(でんどうき)- Electric motor', '電圧(でんあつ)- Voltage', '作業(さぎょう)- Occupation'] | {電気}{工事}士法において、一般用{電気}工{作物}の{工事}又は{作業}で{電気}{工事}士でなければ{従事}できないものは。 | {電圧}600V{以下}で{使用}する{電動機}の{端子}にキャブタイヤケーブルをねじ止めする。 | 火災感知器に{使用}する{小型}{変圧器}（二次{電圧}が36V{以下}）二次側の{配線}をする。 | {電線}を支持する柱を{設置}する。 | {配電盤}を造営材に取り付ける。 |  | 2017_2, 2016_1, 2015_2,
29 | Among the following wiring devices subject to the Electrical Appliance and Material Safety Law, which one is correct as a combination of specific electrical appliances? However, from the rated voltage, rated current, number of poles, etc., it is assumed that all electrical appliances are stipulated by the "Electrical Appliance and Material Safety Law". |  | Tumbler switch, knife switch with cover | Electromagnetic switch, float switch | Lighting duct, plug-in connector | Time switch, circuit breaker for wiring | 4 | ['電磁(でんじ)- Electromagnetic', '開閉器(かいへいき)- Switch', '電流(でんりゅう)- Electric current', '定格(ていかく)- Rated value', '適用(てきよう)- Applying'] | {電気}{用品}安全法の{適用}を受ける次の{配線}{器具}のうち、{特定}{電気}{用品}の{組合せ}として、{正しい}ものは。 ただし、{定格}{電圧}、{定格}{電流}、{極}数等から{全て}が「{電気}{用品}安全法」に定める{電気}{用品}であるとする。 | タンブラ一{スイッチ}、カバー付ナイフ{スイッチ} | {電磁}{開閉器}、フロート{スイッチ} | ライティングダクト、差込み{接続}器 | タイム{スイッチ}、{配線}用{遮断器} |  | 2015_2,
30 | What is the correct statement regarding general electric equipment? However, the voltage of the power generation equipment shall be 600V or less. |  | Equipment that receives power at low voltage is treated as a general-use electric facility even if a small-output power generation facility is installed on the same premises. | Those that receive power at low voltage are considered electric facilities for general use, even if a solar cell power generation facility with an output of 55 kW is installed on the same premises. | Anything that receives high-voltage power is considered a general-purpose electric facility, regardless of the capacity of the received power or the type of industry in which it is demanded. | Even if it receives electricity at a high voltage, it may become a general-use electric facility depending on the industry of the place of demand. | 1 | ['需要(じゅよう)- Demand', '容量(ようりょう)- Capacity', '高圧(こうあつ)- High pressure', '施設(しせつ)- Institution', '設備(せつび)- Equipment', '発電(はつでん)- Electricity generation', '電気工(でんきこう)- Electrician'] | 一般用{電気}工{作物}に関する{記述}として、{正しい}ものは。 ただし、{発電}{設備}は{電圧}600V{以下}とする。 | {低圧}で{受電}するものは、小{出力}{発電}{設備}を同一{構内}に{施設}しても、一般用{電気}工{作物}となる。 | {低圧}で{受電}するものは、{出力}55kWの太陽{電池}{発電}{設備}を同一{構内}に{施設}しても、一般用{電気}工{作物}となる。 | {高圧}で{受電}するものは、{受電}{電力}の{容量}、{需要}{場所}の業{種}にかかわらず、すべて一般用{電気}工{作物}となる。 | {高圧}で{受電}するものであっても、{需要}{場所}の業{種}によっては、一般用{電気}工{作物}になる{場合}がある。 |  | 2015_2,
31 | What is the appropriate construction method for the part shown in ①? |  | Metal pipe work | Metal flexible conduit work | Metal wire work | Cable work using 600V vinyl insulated vinyl sheath cable round shape | 4 | ['工事(こうじ)- Construction work', '円形(えんけい)- Round shape'] | ①で{示す}{部分}の{工事}{方法}として、{適切}なものは。 | {金属}{管}{工事} | {金属}可とう{電線}{管}{工事} | {金属}{線}ぴ{工事} | 600Vビニル{絶縁}ビニルシースケーブル丸形を{使用}したケーブル{工事} |  | 2016_1, 2015_2,
32 | What is the installation position of the equipment indicated by ②? |  | Patio payment | Wall payment | Bed payment | Patio Buried | 2 | ['天井(てんじょう)- Eiling ', '記号(きごう)- Symbol'] | ②で{示す}{図}{記号}の{器具}の取り付け{位置}は。 | {天井}付 | {壁}付 | {床}付 | {天井}埋込 |  | 2015_2,
33 | What is the type of equipment for the symbol shown in ③? |  | Outlet with ground terminal | Outlet with ground terminal and ground terminal | Outlet with ground pole | Outlet with earth leakage breaker | 2 | ['接地(せっち)- Ground (electricity)', '種類(しゅるい)- Variety'] | ③で{示す}{図}{記号}の{器具}の{種類}は。 | {接地}{端子}付{コンセント} | {接地}{極}付{接地}{端子}付{コンセント} | {接地}{極}付{コンセント} | {漏電}{遮断器}付{コンセント} |  | 2019_2, 2019_1, 2015_2,
34 | What is the name of the symbol shown in ④? |  | Metal wire | Floor duct | Lighting duct | Synthetic resin wire | 3 | ['図(ず)- Drawing', '名称(めいしょう)- Name; title'] | ④で{示す}{図}{記号}の{名称}は。 | {金属}{線}ぴ | フロアダクト | ライティングダクト | {合成}樹脂{線}ぴ |  | 2015_2, 2015_1,
35 | What is the maximum voltage [V] that can be used in the small force circuit shown in ⑤? |  | 24 | 30 | 40 | 60 | 4 | ['最大値(さいだいち)- Global maximum', '使用(しよう)- Use; application', '回路(かいろ)- Circuit'] | ⑤で{示す}{部分}の小{勢力}{回路}で{使用}できる{電圧}の{最大値}〔V〕は。 | 24 | 30 | 40 | 60 |  | 2015_2,
36 | What is the name of the symbol shown in ⑥? |  | Joint box | Joint box for VVF | Pull box | Junction box | 2 | ['示す(しめ) -To point out'] | ⑥で{示す}{図}{記号}の{名称}は。 | ジョイントボックス | VVF用ジョイントボックス | プルボックス | ジャンクションボックス |  | 2015_2,
37 | What is the minimum number of wires (number of cores) for the part indicated by ⑦? However, wire the ground side wire from the power supply to the lighting equipment without going through the switch. |  | 2 | 3 | 4 | 5 | 2 | ['部分(ぶぶん)- Portion', '電源(でんげん)- Electrical power', '最少(さいしょう)- Fewest'] | ⑦で{示す}{部分}の{最少}{電線}{本数}（心線数）は。ただし、{電源}からの{接地}側{電線}は、{スイッチ}を経由しないで照明{器具}に{配線}する。 | 2 | 3 | 4 | 5 |  | 2015_2,
38 | What is the name of the symbol (◆) shown in ⑧? |  | General type flasher | General type dimmer | Wide handle type flasher | Wide type dimmer | 3 | ['点滅器(てんめつき)- Switch', '調光器(ちょうこうき)- Dimmer'] | ⑧で{示す}{図}{記号}（◆）の{名称}は。 | 一般形{点滅器} | 一般形{調光器} | ワイドハンドル形{点滅器} | ワイド形{調光器} |  | 2018_1, 2015_2,
39 | What is the minimum allowable value [MΩ] for the insulation resistance between the electric circuit and the ground in the part indicated by ⑨? |  | 0.1 | 0.2 | 0.3 | 0.4 | 1 | ['絶縁抵抗(ぜつえんていこう)- Insulation resistance', '部分(ぶぶん)- Portion', '電路(でんろ)- Electrical circuit'] | ⑨で{示す}{部分}の{電路}と{大地}間の{絶縁}抵抗として、{許容}される{最小}{値}〔MΩ〕は。 | 0.1 | 0.2 | 0.3 | 0.4 |  | 2019_1, 2017_2, 2016_1, 2015_2, 2015_1,
40 | What is the type of grounding work for the part indicated by ⑩? |  | Type A grounding fortifications | Type B grounding fortifications | Type C grounding fortifications | Type D grounding fortifications | 4 | ['種類(しゅるい)- Variety', '部分(ぶぶん)- Portion'] | ⑩で{示す}{部分}の{接地}{工事}の{種類}は。 | A{種}{接地}{工事} | B{種}{接地}{工事} | C{種}{接地}{工事} | D{種}{接地}{工事} |  | 2015_2,
41 | The one with the symbol shown in ⑪. |  | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D | 1 | ['記号(きごう)- Symbol'] | ⑪で{示す}{図}{記号}のものは。 | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D |  | 2019_2, 2019_1, 2015_2,
42 | As for the equipment with the symbol shown in ⑫. |  | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D | 2 | ['器具(きぐ)- Utensil; implement; tool'] | ⑫で{示す}{図}{記号}の{器具}は。 | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D |  | 2017_1, 2015_2,
43 | As for the equipment with the symbol shown in ⑬. |  | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D | 4 | ['器具(きぐ)- Instrument'] | ⑬で{示す}{図}{記号}の{器具}は。 | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D |  | 2017_1, 2015_2,
44 | What is the equipment with the symbol shown in ⑭? |  | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D | 3 | ['記号(きごう)- Sign (semiotics)'] | ⑭で{示す}{図}{記号}の{器具}は。 | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D |  | 2019_1, 2015_2,
45 | What cables are necessary for the wiring work of the part indicated by ⑮? However, the number of core wires of the cable used shall be the minimum. |  | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D | 2 | ['必要(ひつよう)- Necessary', '最少(さいしょう)- Fewest', '配線工事(はいせんこうじ)- Wiring work'] | ⑮で{示す}{部分}の{配線}{工事}に{必要}なケーブルは。ただし、{使用}するケーブルの心線数は{最少}とする。 | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D |  | 2015_2,
46 | If all the connections in the box shown in ⑯ ​​are plug-in connectors, what is the appropriate combination of the type and minimum number of plug-in connectors to be used? However, the wires to be used shall be VVF1.6, and all wires passing through the box shall have connection points. |  | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D | 1 | ['接続(せつぞく)- Connection', '場合(ばあい)- Situation', '種類(しゅるい)- Variety', '接続(せつぞく)- Connection'] | ⑯で{示す}ボックス内の{接続}をすベて差込形{コネクタ}とする{場合}、{使用}する差込形{コネクタ}の{種類}と{最少}{個数}の{組合せ}で、{適切}なものは。ただし、{使用}する{電線}はVVF1.6とし、ボックスを経由する{電線}は、すべて{接続}{箇所}を設けるものとする。 | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D |  | 2015_2,
47 | What is the appropriate combination of the type and minimum number of ring sleeves to be used when all the connections in the box shown in ⑰ are crimp connections? However, the wires to be used shall be VVF1.6, and all wires passing through the box shall have connection points. |  | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D | 3 | ['箇所(かしょ)- Part; spot', '接続(せつぞく)- Connection', '電線(でんせん)- Electric line', '圧着(あっちゃく)- Pressure bonding'] | ⑰で{示す}ボックス内の{接続}をすべて{圧着}{接続}とする時、{使用}するリングスリーブの{種類}と{最少}{個数}の{組合せ}で、{適切}なものは。 ただし、{使用}する{電線}はVVF1.6とし、ボックスを経由する{電線}は、すべて{接続}{箇所}を設けるものとする。 | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D |  | 2015_2,
48 | In this wiring diagram, which switch is not used? However, the diagram below the photo shows the configuration of the contacts. |  | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D | 4 | ['接点(せってん)- Contact (electrical, etc.)', '配線図(はいせんず)- Wiring diagram'] | この{配線}{図}で、{使用}されていない{スイッチ}は。ただし、{写真}下の{図}は、{接点}の{構成}を{示す}。 | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D |  | 2019_2, 2017_2, 2016_1, 2015_2,
49 | In the construction of the second floor part of this wiring diagram, what is not generally used? |  | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D | 3 | ['部分(ぶぶん)- Portion', '施工(せこう)- Construction'] | この{配線}{図}の2階{部分}の{施工}で、{一般的}に{使用}されることのないものは。 | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D |  | 2016_1, 2015_2,
50 | In the construction of this wiring diagram, what is not commonly used. |  | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D | 2 | ['使用(しよう)- Use', '一般的(いっぱんてき)- General'] | この{配線}{図}の{施工}で、{一般的}に{使用}されることのないものは。 | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D |  | 2018_1, 2016_1, 2015_2,