## Sheet1
no | Eng | Picture | Option_1_Eng | Option_2_Eng | Option_3_Eng | Option_4_Eng | Ans | Vocab | Jpn | Option_1_Jpn | Option_2_Jpn | Option_3_Jpn | Option_4_Jpn | Exp | comment
1 | In the circuit shown in the figure, the combined resistance [ Ω ] between terminals a and b is | Picture_1 | 1.1 | 2.5 | 6 | 15 | 2 | ['合成(ごうせい)- Combining', '回路(かいろ)- Circuit'] | {図}のような{回路}で、{端子}a-b間の{合成}抵抗[ Ω ]は。 | 1.1 | 2.5 | 6 | 15 | R₁ = 1/3×3＝3/3＝1Ω R₂ = 1/3×2＝2/3＝1.5Ω So, R₁ + R₂ = 1+1.5＝2.5Ω | 2018_2, 2016_1, 2017_1,
2 | In the AC circuit shown in the figure, the voltage V [ V ] across a 12Ω resistor is: | Picture_2 | 86 | 114 | 120 | 160 | 3 | ['電圧(でんあつ)- Voltage', '両端(りょうたん)- Both ends', '交流(こうりゅう)- Alternating current; AC'] | {図}のような{交流}{回路}において、抵抗12Ωの{両端}の{電圧}V[ V ]は。 | 86 | 114 | 120 | 160 | Z = √(12^2 + 16^2) = √400 = 20Ω I [A] = 200 [V] ÷ 20 Ω = 10 A V = 10A x 12Ω = 120V | 2019_1, 2018_2, 2017_2, 2016_1,
3 | What is wrong about the resistance and allowable current of vinyl insulated wire (single wire)? |  | The allowable current increases as the ambient temperature rises. | The allowable current increases as the diameter of the conductor increases. | The resistance of a wire is proportional to the length of the conductor. | The resistance of a wire is inversely proportional to the square of the diameter of the conductor. | 1 | ['導体(どうたい)- Conductor', '電流(でんりゅう)- Electric current', '抵抗(ていこう)- Resistance', '絶縁(ぜつえん)- Insulation'] | ビニル{絶縁}{電線}（単線）の抵抗と{許容}{電流}に関する{記述}として、誤っているものは。 | {許容}{電流}は、{周囲}の{温度}が上昇すると、大きくなる。 | {許容}{電流}は、{導体}の{直径}が大きくなると、大きくなる。 | {電線}の抵抗は、{導体}の{長さ}に比例する。 | {電線}の抵抗は、{導体}の{直径}の2乗に反比例する。 |  | 2019_1, 2018_1, 2016_1,
4 | The contact resistance at the connection point became 0.2Ω due to poor connection of the electric wire. What is the amount of heat [ kJ ] generated in one hour from the connection point when a current of 15 A flows through this wire? However, it is assumed that the value of the contact resistance does not change. |  | 11 | 45 | 72 | 162 | 4 | ['熱量(ねつりょう)- Quantity of heat', '不良(ふりょう)- Bad; poor', '接触(せっしょく)- Touch; contact', '電線(でんせん)- Cable'] | {電線}の{接続}{不良}により、{接続}点の{接触}抵抗が0.2Ωとなった。この{電線}に15Aの{電流}が{流れる}と、{接続}点から1時間に{発生}する{熱量}[ kJ ]は。 ただし、{接触}抵抗の{値}は変化しないものとする。 | 11 | 45 | 72 | 162 | V = IR = 0.2 x 15 = 3 V P = VI = 3 x 15 = 45 W Q = 45 x 3600 = 162000W・t = 162kW・t | 2016_1,
5 | When a three-phase induction motor with rated voltage V [V] and rated current I [A] was operated continuously for time t [h], the power consumption was W [kW·h]. The formula for the power factor [%] of this motor is |  | Picture_5_A | Picture_5_B | Picture_5_C | Picture_5_D | 1 | ['状態(じょうたい)- State; condition', '力率(りきりつ)- Power factor', '定格(ていかく)- Rated value'] | {定格}{電圧}V[ V ]、{定格}{電流}I[ A ]の{三相}{誘導電動機}を{定格}{状態}で時間t[ h ]の間、連続運転したところ、消費{電力}量がW[ kW・h ]であった。 この電動機の{力率}[%]を表す式は。 | Picture_5_A | Picture_5_B | Picture_5_C | Picture_5_D |  | 2016_1,
6 | In the single-phase three-wire circuit shown in the figure, when the resistance of each wire is 0.2Ω, the voltage [ V ] between a and b is: | Picture_6 | 96 | 100 | 102 | 106 | 3 | ['回路(かいろ)- Circuit ', '電圧(でんあつ)- Voltage', '電線(でんせん)- Electric cable'] | {図}のような{単相}3線式{回路}において、{電線}1線{当たり}の抵抗が0.2Ωのとき、a-b間の{電圧}[ V ]は。 | 96 | 100 | 102 | 106 | V = IR. V = 10 × 0.2 = 2. Voltage a to b is 104 - 2 = 102V | 2018_1, 2018_2, 2016_1,
7 | In the single-phase three-wire circuit shown in the figure, the two loads with power consumption of 1000W and 200W are both resistive loads. What is the voltage [ V ] between a and b when the wire is broken at the point marked with x in the figure? However, it is assumed that the resistance value of the load does not change due to disconnection. | Picture_7 | 17 | 33 | 100 | 167 | 2 | ['負荷(ふか)- Load (electrical)', '断線(だんせん)- Disconnection', '抵抗(ていこう)- Resistance', '回路(かいろ)- Circuit'] | {図}のような{単相}3線式{回路}において、消費{電力}1000w、200Wの2つの{負荷}はともに抵抗{負荷}である。{図}中の×印点で{断線}した{場合}、a-b間の{電圧}[ V ]は。 ただし、{断線}によって{負荷}の抵抗{値}は変化しないものとする。 | 17 | 33 | 100 | 167 | 200(V)/10(Ω) + 50(Ω) = 200/60≒3.3A the voltage between a and b, 3.3A x 10Ω = 33V | 2019_2, 2016_1,
8 | In low-voltage indoor wiring work using metal pipes, when three 600V vinyl insulated wires (annealed copper wires) with a cross-sectional area of ​​3.5mm2 are installed inside the pipe, what is the allowable current [A] per wire? However, the ambient temperature should be 30°C or less, and the current reduction factor should be 0.70. |  | 19 | 26 | 34 | 49 | 2 | ['減少(げんしょう)- Decrease', '電流(でんりゅう)- Electric current', '絶縁(ぜつえん)- Insulation', '許容(きょよう)- Permission', '低圧(ていあつ)- Low voltage'] | {金属}管による{低圧}{屋内配線}{工事}で、{管内}に{断面積}3.5mm2の600Vビニル{絶縁}{電線}（軟{銅線}）3本を収めて{施設}した{場合}、{電線}1本{当たり}の{許容}{電流}[ A ]は。 ただし、{周囲}{温度}は30℃{以下}、{電流}{減少}{係数}は0.70とする。 | 19 | 26 | 34 | 49 | The permissible current for a stranded wire with a cross-sectional area of ​​3.5㎟ is 37A So, 37×0.70=25.9A = 26A | 2019_2, 2016_1,
9 | As shown in the figure, when branching from a low-voltage indoor main line protected by an overcurrent circuit breaker with a rated current of 50A and installing an overcurrent circuit breaker at a position of 7m, the minimum allowable current of the wire between a and b [A] teeth. | Picture_9 | 12.5 | 17.5 | 22.5 | 27.5 | 2 | ['最小値(さいしょうち)- Minimum value', '過電流(かでんりゅう)- Over current', '屋内(おくない)- Indoor', '遮断器(しゃだんき)- Circuit breaker'] | {図}のように{定格}{電流}50Aの過{電流}{遮断器}で保護された{低圧}{屋内}{幹線}から{分岐}して、7mの{位置}に過{電流}{遮断器}を{施設}するとき、a-b間の{電線}の{許容}{電流}の{最小}{値}[ A ]は。 | 12.5 | 17.5 | 22.5 | 27.5 |  | 2019_2, 2019_1, 2018_1, 2018_2, 2016_2, 2016_1, 2015_1, 2015_2,
10 | In the design of branch circuits for low-voltage indoor wiring, what is the appropriate combination of circuit breakers, branch circuit wire thicknesses, and outlets? However, the distance from the branch point to the circuit breaker for wiring is 3m, and the distance from the circuit breaker for wiring to the outlet is 8m. Also, the outlet shall not be a dual-purpose outlet. |  | 1 outlet with rated current of 20A | 1 outlet with rated current of 30A | 2 outlets with rated current of 15A | 2 outlets with rated current of 20A | 4 | ['屋内配線(おくないはいせん)- Interior wiring', '兼用(けんよう)- Multi-use', '分岐点(ぶんきてん)- Junction', '分岐(ぶんき)- Divergence'] | {低圧}{屋内配線}の{分岐}{回路}の{設計}で、配線用{遮断器}、{分岐}{回路}の{電線}の太さ及び{コンセント}の{組合せ}として、{適切}なものは。 ただし、{分岐}点から配線用{遮断器}までは3m、配線用{遮断器}から{コンセント}までは8mとし、{電線}の{数値}は{分岐}{回路}の{電線}（軟{銅線}）の太さを{示す}。 また、{コンセント}は{兼用}{コンセント}ではないものとする。 | Figure_10_A#{定格}{電流} 20Aの {コンセント} 1個 | Figure_10_B#{定格}{電流} 30Aの {コンセント} 1個 | Figure_10_C#{定格}{電流} 15Aの {コンセント} 2個 | Figure_10_D#{定格}{電流} 20Aの {コンセント} 2個 |  | 2019_2, 2017_2, 2016_2, 2016_1, 2015_2, 2015_1,
11 | What is the appropriate combination of the type of electrical work and the equipment used in that work? |  | Metal wire work and bolt clippers | Synthetic resin pipe work and pipe benders | Metal pipe work and click balls | Bus duct work and crimping pliers | 3 | ['工事(こうじ)- Construction work', '種類(しゅるい)- Type; category'] | {電気}{工事}の{種類}と、その{工事}で{使用}するエ具の{組合せ}として、{適切}なものは。 | {金属}{線}ぴ{工事}とボルトクリッパ | {合成}樹脂{管}{工事}とパイプベンダ | {金属}{管}{工事}とクリックボール | バスダクト{工事}と{圧着}ペンチ |  | 2018_2, 2017_2, 2016_1,
12 | Inappropriate usage of the outlet box (made of metal). |  | Used to make it easier to pull in electric wires in metal pipe work. | Used when pulling out electric wires at the part where lighting fixtures are installed. | Used for connecting electric wires in metal pipe work. | Used to collectively install circuit breakers for wiring. | 4 | ['工事(こうじ)- Construction work', '電線(でんせん)- Electric cable', '金属製(きんぞくせい)- Made of metal'] | アウトレットボックス（{金属}製）の{使用}{方法}として、{不適切}なものは。 | {金属}{管}{工事}で{電線}の引き入れを{容易}にするのに用いる。 | 照明{器具}などを取り付ける{部分}で{電線}を引き出す{場合}に用いる。 | {金属}{管}{工事}で{電線}{相互}を{接続}する{部分}に用いる。 | {配線}用{遮断器}を{集合}して{設置}するのに用いる。 |  | 2019_1, 2017_2, 2016_1,
13 | What is the maximum permissible temperature [°C] of insulation for 600V vinyl insulated wires (IV) used as low-voltage indoor wiring? |  | 30 | 45 | 60 | 75 | 3 | ['温度(おんど)- Temperature', '絶縁(ぜつえん)- Insulation'] | {低圧}{屋内配線}として{使用}する600Vビニル{絶縁}{電線}（IV）の{絶縁}{物の}最高{許容}{温度}[℃ ]は。 | 30 | 45 | 60 | 75 |  | 2018_1, 2016_1,
14 | How to reverse the rotation of a three-phase induction motor. |  | Swap all three connections of the three-phase power supply. | Replace any two of the three connections of the three-phase power supply. | Install the capacitor. | Install the star-delta starter. | 2 | ['逆回転(ぎゃくかいてん)- Spinning the opposite way'] | {三相}{誘導電動機}を逆{回転}させるための{方法}は。 | {三相}{電源}の3本の結{線}を3本とも入れ替える。 | {三相}{電源}の3本の結{線}のうち、いずれか2本を入れ替える。 | コンデンサを取り付ける。 | スターデルタ{始動}器を取り付ける。 |  | 2016_1,
15 | What is suitable for lighting in places with thick fog or in tunnels? |  | Sodium lamp | Fluorescent lamp | Halogen lamp | Mercury lamp | 1 | ['場所(ばしょ)- Place', '水銀(すいぎん)- Mercury (element)'] | 霧の濃い{場所}やトンネル内等の照明に適しているものは。 | ナトリウムランプ | 蛍光ランプ | ハロゲン{電球} | {水銀}ランプ |  | 2016_1,
16 | What are the uses of the material shown in the photo? | Picture_16 | Used where the VVF cable is connected. | Used to attach switches and outlets. | Used for wire connections in synthetic resin pipe construction. | Used when hanging the cord from the ceiling. | 1 | ['材料(ざいりょう)- Materials; ingredients', '電線(でんせん)- Electric cable'] | {写真}に{示す}{材料}の{用途}は。 | VVFケーブルを{接続}する{箇所}に用いる。 | {スイッチ}や{コンセント}を取り付けるのに用いる。 | {合成}樹脂{管}{工事}において、{電線}を{接続}する{箇所}に用いる。 | {天井}からコードを吊り下げるときに用いる。 |  | 2016_1,
17 | What is the name of the instrument shown in the photo? | Picture_17 | Wiring circuit breaker | Earth leakage circuit breaker | Electromagnetic contactor | Earth leakage alarm | 2 | ['電磁(でんじ)- Electromagnetic', '写真(しゃしん)- Photography'] | {写真}に{示す}{器具}の{名称}は。 | {配線}用{遮断器} | {漏電}{遮断器} | {電磁}{接触}器 | {漏電}{警報器} |  | 2016_1,
18 | What is the purpose of the tool shown in the photo? | Picture_18 | Used for bending metal pipes. | Used for connecting synthetic resin flexible conduits. | Used for bending lighting ducts. | Used for bending rigid PVC conduits. | 4 | ['厚さ(あつ)- Thickness', '電線(でんせん)- Electric cable', '金属(きんぞく)- Metal', '工具(こうぐ)- Hand tool'] | {写真}に{示す}{工具}の{用途}は。 | {金属}{管}の曲げ加工に用いる。 | {合成}樹脂製可とう{電線}{管}の{接続}加工に用いる。 | ライティングダクトの曲げ加工に用いる。 | {硬質}塩化ビニル{電線}{管}の曲げ加工に用いる。 |  | 2019_1, 2016_1,
19 | In low-voltage indoor wiring work using 600V vinyl-insulated vinyl-sheathed flat cables of 1.6 mm, what is inappropriate for the insulation treatment of the end connections between insulated wires? However, the vinyl tape shall be an insulating tape with a thickness of about 0.2mm specified by JIS. |  | Connect with a ring sleeve, wrap the connecting part with self-adhesive insulating tape (thickness of about 0.5 mm) over half the width and wrap it once (2 layers), and then wrap the protective tape (about 0.2 mm thick) at least half the width. Wrapped once (2 layers). | Connected with a ring sleeve, and wrapped twice (4 layers) with black adhesive polyethylene insulating tape (thickness: about 0.5 mm) over half the width. | Connected with a ring sleeve and wrapped once (2 layers) with vinyl tape over half the width or more. | Connection was made using a plug-in connector, and the connecting part was not wrapped with vinyl tape. | 3 | ['接続(せつぞく)- Connection ', '絶縁テープ(ぜつえんテープ)- Electrical tape', '半幅(はんはば)- Half-width cloth', '部分(ぶぶん)- Portion', '絶縁(ぜつえん)- Insulation'] | 600Vビニル{絶縁}ビニルシースケーブル平形1.6mmを{使用}した{低圧}{屋内配線}{工事}で、{絶縁}{電線}{相互}の{終端}{接続}{部分}の{絶縁}処理として、{不適切}なものは。 ただし、ビニルテープはJISに定める{厚さ}約0.2mmの{絶縁}テープとする。 | リングスリープにより{接続}し、{接続}{部分}を自己融着性{絶縁}テープ（{厚さ}約0.5mm）で{半幅}以上重ねて1回（2層）巻き、更に保護テープ（{厚さ}約0.2mm）を{半幅}以上重ねて1回（2層）巻いた。 | リングスリーブにより{接続}し、{接続}{部分}を黒色粘着性ポリエチレン{絶縁}テープ（{厚さ}約0.5mm）で{半幅}以上重ねて2回（4層）巻いた。 | リングスリーブにより{接続}し、{接続}{部分}をビニルテープで{半幅}以上重ねて1回（2層）巻いた。 | 差込形{コネクタ}により{接続}し、{接続}{部分}をビニルテープで巻かなかった。 |  | 2016_1, 2015_2,
20 | When grounding a three-phase induction motor with a rated voltage of 200 V and a rated output of 2.2 kW fixed to the floor, what is an inappropriate combination of the thickness of the ground wire (annealed copper wire) and the ground resistance value? However, earth leakage circuit breakers shall not be installed. |  | Diameter 2.6mm, 75Ω | Diameter 2.0mm, 50Ω | Diameter 1.6mm, 10Ω | Nominal cross-sectional area 0.75mm2, 5Ω | 4 | ['直径(ちょっけい)- Diameter', '接地(せっち)- Ground (electricity)', '出力(しゅつりょく)- Output', '電圧(でんあつ)- Voltage', '床(ゆか)- Floor'] | {床}に固定した{定格}{電圧}200V、{定格}{出力}2.2kWの{三相}{誘導電動機}の鉄台に{接地}{工事}をする{場合}、{接地}線（軟{銅線}）の太さと{接地}抵抗{値}の{組合せ}で、{不適切}なものは。 ただし、{漏電}{遮断器}を{設置}しないものとする。 | {直径}2.6mm 、 75Ω | {直径}2.0mm 、 50Ω | {直径}1.6mm 、 10Ω | {公称}{断面積}0.75mm2 、 5Ω |  | 2019_1, 2016_1,
21 | What is the appropriate construction method for cable construction using 600V vinyl-insulated vinyl-sheathed cable for 100/200V low-voltage indoor wiring work? |  | The length of the metal pipe used as a protective device was 10m, but the metal pipe was not grounded because it was in a dry place. | A round cable was bent with the inside radius of the bending portion being 6 times the outside diameter of the cable. | Buried directly in the concrete wall of the building. (Except for temporary wiring work.) | Housed in the same synthetic resin tube together with low-current electric wires for telephones without metal shielding layers. | 2 | ['直接(ちょくせつ)- Direct; immediate', '外径(がいけい)- Outer diameter', '内側(うちがわ)- Interior', '工事(こうじ)- construction work'] | 100/200Vの{低圧}{屋内配線}{工事}で、600Vビニル{絶縁}ビニルシースケーブルを用いたケーブル{工事}の{施工}{方法}として、{適切}なものは。 | {防護}装置として{使用}した{金属}{管}の{長さ}が10mであったが、乾燥した{場所}であるので、{金属}{管}にD{種}{接地}{工事}を施さなかった。 | 丸形ケーブルを、屈曲部の{内側}の半径をケーブル{外径}の6倍にして曲げた。 | 建{物の}コンクリート{壁}の中に{直接}埋設した。（臨時{配線}{工事}の{場合}を除く。） | {金属}製遮へい層のない{電話}用弱{電流}{電線}と共に同一の{合成}樹脂{管}に収めた。 |  | 2016_1,
22 | What is inappropriate as a construction method for low-voltage indoor wiring with a working voltage of 300 V or less? |  | In flexible metal conduit work, stranded wires (600V vinyl insulated wires) were used, and were housed without connecting parts inside the pipe. | When branching electric wires in floor duct work, apply sufficient insulating coating to the joints and place the joints in a junction box so that the joints can be easily inspected. | When branching electric wires in metal duct work, the joints were covered with sufficient insulating coating, and the joints were placed in the duct so that they could be easily inspected. | In the lighting duct construction, the end of the duct was installed without blockage. | 4 | ['終端部(しゅうたんぶ)- Trailer', '点検(てんけん)- Inspection', '接続(せつぞく)- Connection', '方法(ほうほう)- Method', '低圧(ていあつ)- Low voltage'] | {使用}{電圧}300V{以下}の{低圧}{屋内配線}の{工事}{方法}として、{不適切}なものは。 | {金属}可とう{電線}管{工事}で、{より線}（600Vビニル{絶縁}{電線}）を用いて、{管内}に{接続}{部分}を設けないで収めた。 | フロアダクト{工事}で、{電線}を{分岐}する{場合}、{接続}{部分}に十分な{絶縁}{被覆}を施し、かつ、{接続}{部分}を{容易}に{点検}できるようにして{接続}箱（ジャンクションボックス）に収めた。 | {金属}ダクト{工事}で、{電線}を{分岐}する{場合}、{接続}{部分}に十分な{絶縁}{被覆}を施し、かつ、{接続}{部分}を{容易}に{点検}できるようにしてダクトに収めた。 | ライティングダクト{工事}で、ダクトの{終端部}は閉そくしないで{施設}した。 |  | 2016_1,
23 | What is inappropriate as a method of indoor wiring work for installing a room air conditioner with a three-phase 200V rated power consumption of 2.8kW in a house with a store? |  | Install an earth leakage circuit breaker in the electric circuit. | Install a dedicated wiring circuit breaker in the electric circuit. | Apply simple touch protection measures to indoor wiring. | Connect the room air conditioner with indoor wiring and an outlet. | 4 | ['簡易(かんい)- Convenience', '防護(ぼうご)- Protection'] | {店舗}付き{住宅}に{三相}200V、{定格}消費電カ2.8kWのルームエアコンを{施設}する{屋内配線}{工事}の{方法}として、{不適切}なものは。 | {電路}には{漏電}{遮断器}を{施設}する。 | {電路}には{専用}の{配線}用{遮断器}を{施設}する。 | {屋内配線}には、{簡易}{接触}{防護}{措置}を施す。 | ルームエアコンは{屋内配線}と{コンセント}で{接続}する。 |  | 2016_1,
24 | What inspections are not generally performed when low-voltage indoor wiring work for general-purpose electric facilities is completed? |  | Absolute endurance test | Determination of absolute resistance | Determination of ground resistance | Visual point of view | 1 | ['測定(そくてい)- Measurement', '検査(けんさ)- Inspection', '電気工(でんきこう)- Electrician'] | ―般用{電気}工{作物}の{低圧}{屋内配線}{工事}が完了したときの{検査}で、一般に行われていないものは。 | {絶縁}耐力試験 | {絶縁}抵抗の{測定} | {接地}抵抗の{測定} | 目視{点検} |  | 2016_1, 2015_2,
25 | What is the appropriate method to open the branch switch to completely separate the load from the power supply and measure the insulation resistance between the low-voltage indoor electric circuit on the load side and the ground all at once? |  | Turn on all flashers on the load side, and measure loads that are normally connected to wiring while in use. | Turn off all flashers on the load side, and measure the load that is normally connected to the wiring while in use. | Turn on all flashers on the load side, remove all loads that are always connected to the wiring, and measure. | Turn off all flashers on the load side and remove all loads that are normally connected to the wiring before measuring. | 1 | ['常時(じょうじ)- Usually', '点滅器(てんめつき)- Switch', '低圧(ていあつ)- Low voltage', '開放(かいほう)- Opening'] | {分岐}{開閉器}を{開放}して{負荷}を{電源}から完全に分離し、その{負荷}側の{低圧}{屋内}{電路}と{大地}間の{絶縁}抵抗を一括{測定}する{方法}として、{適切}なものは。 | {負荷}側の{点滅器}をすべて「入」にして、{常時}{配線}に{接続}されている{負荷}は、{使用}{状態}にしたままで{測定}する。 | {負荷}側の{点滅器}をすべて「切」にして、{常時}{配線}に{接続}されている{負荷}は、{使用}{状態}にしたままで{測定}する。 | {負荷}側の{点滅器}をすべて「入」にして、{常時}{配線}に{接続}されている{負荷}は、すべて取り外して{測定}する。 | {負荷}側の{点滅器}をすべて「切」にして、{常時}{配線}に{接続}されている{負荷}は、すべて取り外して{測定}する。 |  | 2019_2, 2016_1,
26 | When using a direct-reading earth resistance meter (earth tester) to measure the earth resistance by direct reading, what is the appropriate placement of the auxiliary earth electrodes (2 places)? |  | With the earth electrode to be measured at the end, place two auxiliary earth electrodes on a straight line one after another about 1m apart. | With the ground electrode to be measured in the center, place auxiliary ground electrodes in a straight line on the left and right with a distance of about 5 m. | With the earth electrode to be measured at the end, place two auxiliary earth electrodes on a straight line one after another about 10m apart. | Arrange the earth electrode to be measured and two auxiliary earth electrodes about 5m apart from each other in an equilateral triangle. | 3 | ['測定(そくてい)- Measurement', '程度(ていど)- Standard', '補助(ほじょ)- Assistance', '抵抗(ていこう)- Resistance'] | 直読式{接地}抵抗計（{アース}テスタ）を{使用}して直読で{接地}抵抗を{測定}する{場合}、{補助}{接地}{極}（2{箇所}）の{配置}として、{適切}なものは。 | 被{測定}{接地}{極}を端とし、一直{線}上に2{箇所}の{補助}{接地}{極}を順次1m{程度}離して{配置}する。 | 被{測定}{接地}{極}を{中央}にして、左右一直{線}上に{補助}{接地}{極}を5m{程度}離して{配置}する。 | 被{測定}{接地}{極}を端とし、一直{線}上に2{箇所}の{補助}{接地}{極}を順次10m{程度}離して{配置}する。 | 被{測定}{接地}{極}と2{箇所}の{補助}{接地}{極}を{相互}に5m{程度}離して正三角形に{配置}する。 |  | 2016_1,
27 | There is a symbol as shown in the figure on the scale plate of the electric meter. What is the correct meaning of the symbols and which circuits can be measured? | Picture_27 | Use in an AC circuit with the scale plate placed horizontally in the movable iron type. | Use in an AC circuit with the scale plate placed horizontally in the moving coil type. | Use in a direct current circuit with a movable iron plate with a vertical scale plate. | Use in a DC circuit with the scale plate placed horizontally on the moving coil type. | 4 | ['問題(もんだい)- Problem', '交流(こうりゅう)- Exchange', '可動(かどう)- Moveable', '回路(かいろ)- Circuit'] | {電気}{計器}の目盛板に{図}のような{記号}がある。 {記号}の意味及び{測定}できる{回路}で、{正しい}ものは。 | {可動}鉄片形で目盛板を{水平}に置いて、{交流}{回路}で{使用}する。 | {可動}{コイル}形で目盛板を{水平}に置いて、{交流}{回路}で{使用}する。 | {可動}鉄片形で目盛板を鉛直に立てて、{直流}{回路}で{使用}する。 | {可動}{コイル}形で目盛板を{水平}に置いて、{直流}{回路}で{使用}する。 |  | 2016_1,
28 | What are the incorrect statements regarding the duties or limitations of electricians? |  | An electrician must carry an electrician's license when engaging in electrical work as stipulated by the Electrician Law. | Electrical workers shall, when engaging in electrical work as stipulated by the Electrician Law, comply with ministerial ordinances that stipulate technical standards for electrical equipment. | When an electrician changes his/her address, he/she must apply to the prefectural governor who issued the license and have the license rewritten. | Electrical workers must use electrical appliances and materials specified by the Electrical Appliance and Material Safety Law for electrical work that are properly marked. | 3 | ['同法(どうほう)- Same method, Law', '住所(じゅうしょ)- Address', '作業(さぎょう)- Occupation', '免状(めんじょう)- Diploma; licence', '記述(きじゅつ)- Description', '電気工事士(でんきこうじし)- Licensed electrician'] | {電気}{工事}士の{義務}又は{制限}に関する{記述}として、誤っているものは。 | {電気}{工事}士は、{電気}{工事}士法で定められた{電気}{工事}の{作業}に{従事}するときは、{電気}{工事}士{免状}を携帯していなければならない。 | {電気}{工事}士は、{電気}{工事}士法で定められた{電気}{工事}の{作業}に{従事}するときは、{電気}{設備}に関する{技術基準}を定める{省令}に適合するようにその{作業}をしなければならない。 | {電気}{工事}士は、{住所}を変更したときは、{免状}を交付した都{道}府県知事に申請して{免状}の書換えをしてもらわなければならない。 | {電気}{工事}士は、{電気}{工事}の{作業}に{電気}{用品}安全法に定められた{電気}{用品}を{使用}する{場合}は{同法}に定める適正な{表示}が付されたものを{使用}しなければならない。 |  | 2016_1,
29 | According to the Electrician Law, construction or work of electrical facilities for general use that can only be carried out by an electrician. |  | Attach a power meter that will be used at a voltage of 600V or less. | Wire the secondary side of the small transformer (secondary voltage is 36V or less) used in the intercom facility. | Install pillars and brackets to support the wires. | Connect the conduit and the box. | 4 | ['腕木(うでぎ)- Crossarm; bracket', '配線(はいせん)- Wiring', '変圧器(へんあつき)- Transformer', '従事(じゅうじ)- Engaging in (work)'] | {電気}{工事}士法において、一般用{電気}工{作物}の{工事}又は{作業}で{電気}{工事}士でなければ{従事}できないものは。 | {電圧}600V{以下}で{使用}する{電力}量計を取り付ける。 | インターホーンの{施設}に{使用}する{小型}{変圧器}（二次{電圧}が36V{以下}）の二次側の{配線}をする。 | {電線}を支持する柱、{腕木}を{設置}する。 | {電線}{管}とボックスを{接続}する。 |  | 2017_2, 2016_1, 2015_2,
30 | Of the following electrical appliances subject to the Electrical Appliance and Material Safety Law, the specified electrical appliances are: |  | Leakage circuit breaker with fixed current of 20A | Power consumption of 30W of exchange fan | Metal wire tube with outer diameter of 19mm | Power consumption of 40W 雍光ランプ | 1 | ['金属製(きんぞくせい)- Made of metal', '電流(でんりゅう)- Electric current', '特定(とくてい)- Specific', '用品(ようひん)- Articles', '適用(てきよう)- Applying'] | {電気}{用品}安全法の{適用}を受ける次の{電気}{用品}のうち、{特定}{電気}{用品}は。 | {定格}{電流}20Aの{漏電}{遮断器} | 消費{電力}30Wの換気扇 | {外径}19mmの{金属}製{電線}{管} | 消費{電力}40Wの蛍光ランプ |  | 2018_2, 2017_1, 2016_1,
31 | The figure is a wiring diagram of a three-story wooden house. What is the name of the graphic symbol indicated by ①? |  | Dimmer | Clear | Delay switch | Remote control switch | 1 | ['配線図(はいせんず)- Wiring diagram', '住宅(じゅうたく)- Residence', '木造(もくぞう)- Wooden'] | {図}は、{木造}3階建{住宅}の{配線}{図}である。 ①で{示す}{図}{記号}の{名称}は。 | {調光器} | 素通し | {遅延}{スイッチ} | リモコン{スイッチ} |  | 2016_1,
32 | What is the correct pole arrangement (blade holder) for the outlet shown in ②? |  | Picture_32_A | Picture_32_B | Picture_32_C | Picture_32_D | 2 | ['配置(はいち)- Arrangement'] | ②で{示す}{コンセント}の{極}{配置}（刃受）で、{正しい}ものは。 | Picture_32_A | Picture_32_B | Picture_32_C | Picture_32_D |  | 2019_1, 2016_1,
33 | What is the appropriate construction method for the part shown in ③? |  | Metal wire work | Metal pipe work | Metal duct work | Cable work using 600V vinyl-insulated vinyl-sheathed round cable | 4 | ['円形(えんけい)- Round shape', '金属(きんぞく)- Metal', '工事(こうじ)- Construction work'] | ③で{示す}{部分}の{工事}{方法}として、{適切}なものは。 | {金属}{線}ぴ{工事} | {金属}{管}{工事} | {金属}ダクト{工事} | 600Vビニル{絶縁}ビニルシースケーブル丸形を{使用}したケーブル{工事} |  | 2016_1, 2015_2,
34 | What is the symbol for the instrument attached to the part indicated by ④? |  | Picture_34_A | Picture_34_B | Picture_34_C | Picture_34_D | 4 | ['計器(けいき)- Meter', '部分(ぶぶん)- Portion; Part'] | ④で{示す}{部分}に取り付ける{計器}の{図}{記号}は。 | Picture_34_A | Picture_34_B | Picture_34_C | Picture_34_D |  | 2016_1,
35 | What is the minimum allowable value [MΩ] for the insulation resistance between the electric circuit and the ground in the part indicated by ⑤? |  | 0.1 | 0.2 | 0.4 | 1 | 1 | ['最小値(さいしょうち)- Minimum value', '電路(でんろ)- Electrical circuit'] | ⑤で{示す}{部分}の{電路}と{大地}間の{絶縁}抵抗として、{許容}される{最小}{値}[ MΩ ]は。 | 0.1 | 0.2 | 0.4 | 1 |  | 2019_1, 2017_2, 2016_1, 2015_2, 2015_1,
36 | What is the name of the symbol shown in ⑥? |  | Ceiling (directly attached to the ceiling) | Embedded fixture | Chandelier | Pendant | 3 | ['名称(めいしょう)- Name; title', '記号(きごう)- Symbol'] | ⑥で{示す}{図}{記号}の{名称}は。 | シーリング（{天井}直付） | 埋込{器具} | シャンデリヤ | ペンダント |  | 2016_1,
37 | What is the permissible maximum value [Ω] of the grounding resistance in the grounding work of the part indicated by ⑦? |  | 100 | 300 | 500 | 600 | 3 | ['最大値(さいだいち) -Global maximum', '接地(せっち)- Ground (electricity)'] | ⑦で{示す}{部分}の{接地}{工事}における{接地}抵抗の{許容}される{最大値}[ Ω ]は。 | 100 | 300 | 500 | 600 |  | 2019_1, 2016_1,
38 | What is the minimum number of wires (number of core wires) for the part indicated by ⑧? |  | 2 | 3 | 4 | 5 | 2 | ['電線(でんせん)- Electric cable', '最少(さいしょう)- Fewest; least'] | ⑧で{示す}{部分}の{最少}{電線}{本数}（心線数）は。 | 2 | 3 | 4 | 5 |  | 2019_1, 2016_1,
39 | What is the name of the symbol shown in ⑨? |  | Automatic flasher | Hot-wire automatic switch | Time switch | Rainproof switch | 1 | ['記号(きごう)- Symbol; code', '自動(じどう)- Automatic'] | ⑨で{示す}{図}{記号}の{名称}は。 | {自動}{点滅器} | 熱{線}式{自動}{スイッチ} | タイム{スイッチ} | 防雨形{スイッチ} |  | 2016_1,
40 | What is the wiring method for the symbols shown in ⑩? |  | Concealed ceiling wiring | Concealed floor wiring | Exposed wiring | Exposed floor wiring | 2 | ['床面(ゆかめん)- Floor; floor surface', '配線(はいせん)- Wiring'] | ⑩で{示す}{図}{記号}の{配線}{方法}は。 | {天井}隠ぺい{配線} | {床}隠ぺい{配線} | 露出{配線} | {床面}露出{配線} |  | 2019_1, 2016_1,
41 | What is the correct combination of ring sleeve type, number, and engraving when the connection work of the part shown in ⑪ is crimped with a ring sleeve? However, the wires used are all VVF1.6, and the ○, small, and medium marks in the center of the ring sleeve shown in the photo represent the stamps after connection. |  | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D | 1 | ['写真(しゃしん)- Photograph', '種類(しゅるい)- Variety; kind', '刻印(こくいん)- Engraving a seal'] | ⑪で{示す}{部分}の{接続}{工事}をリングスリーブで{圧着}{接続}した{場合}のリングスリーブの{種類}、{個数}及び{刻印}との{組合せ}で、{正しい}ものは。 ただし、{使用}する{電線}はすべてVVF1.6とし、{写真}に{示す}リングスリーブ{中央}の〇、小、中は{接続}後の{刻印}を表す。 | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D |  | 2016_1,
42 | As for the equipment with the symbol shown in ⑫. |  | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D | 3 | ['記号(きごう)- Symbol; code', '器具(きぐ)- Utensil; implement'] | ⑫で{示す}{図}{記号}の{器具}は。 | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D |  | 2016_1,
43 | If all the connections in the VVF joint box shown in ⑬ are plug-in connectors, what is the appropriate combination of plug-in connector type and minimum number to be used? However, all wires used shall be VVF1.6. |  | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D | 2 | ['電線(でんせん)- Electric cable', '種類(しゅるい)- Variety; kind', '接続(せつぞく)- Connection'] | ⑬で{示す}VVF用ジョイントボックス内の{接続}をすべて差込形{コネクタ}とする{場合}、{使用}する差込形{コネクタ}の{種類}と{最少}{個数}の{組合せ}で、{適切}なものは。 ただし、{使用}する{電線}はすべてVVF1.6とする。 | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D |  | 2016_1,
44 | What cables are necessary for the wiring work of the part indicated by ⑭? However, the number of core wires of the cable used shall be the minimum. |  | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D | 2 | ['最少(さいしょう)- Fewest; least', '部分(ぶぶん)- Portion; section'] | ⑭で{示す}{部分}の{配線}{工事}に{必要}なケーブルは。 ただし、{使用}するケーブルの心線数は{最少}とする。 | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D |  | 2016_1,
45 | If all the connections in the VVF joint box shown in ⑮ are crimped connections, what is the appropriate combination of ring sleeve type and minimum number to be used? However, all wires used shall be VVF1.6. |  | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D | 3 | ['個数(こすう)- Quantity', '圧着(あっちゃく)- Pressure bonding'] | ⑮で{示す}VVF用ジョイントボックス内の{接続}をすべて{圧着}{接続}とする{場合}、{使用}するリングスリーブの{種類}と{最少}{個数}の{組合せ}で、{適切}なものは。 ただし、{使用}する{電線}はすべてVVF1.6とする。 | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D |  | 2016_1, 2019_1,
46 | In the construction of this wiring diagram, what is not commonly used. |  | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D | 1 | ['配線図(はいせんず)- Wiring diagram'] | この{配線}{図}の{施工}で、{一般的}に{使用}されることのないものは。 | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D |  | 2018_1, 2016_1, 2015_2,
47 | In the construction of this wiring diagram, what is not commonly used. |  | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D | 4 | ['一般的(いっぱんてき)- general; popular'] | この{配線}{図}の{施工}で、{一般的}に{使用}されることのないものは。 | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D |  | 2016_1, 2015_2,
48 | In this wiring diagram, which switch is not used? However, the diagram below the photo shows the configuration of the contacts. |  | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D | 3 | ['構成(こうせい)- Composition', '接点(せってん)- Contact (electrical, etc.)', '施工(せこう)- Work'] | この{配線}{図}で、{使用}されていない{スイッチ}は。 ただし、{写真}下の{図}は、{接点}の{構成}を{示す}。 | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D |  | 2019_2, 2017_2, 2016_1, 2015_2,
49 | Regarding the construction of this wiring diagram, what is the combination of things that are not used? |  | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D | 2 | ['組合(くみあわせ)- Combination'] | この{配線}{図}の{施工}{に関して}、{使用}されることのない{物の}{組合せ}は。 | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D |  | 2016_1,
50 | In this wiring diagram, what is the correct combination of outlets used and their number? |  | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D | 4 | ['個数(こすう)- Quantity'] | この{配線}{図}の{施工}{に関して}、{使用}されることのない{物の}{組合せ}は。 | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D |  | 2016_1, 2016_2,