## Sheet1
no | Eng | Picture | Option_1_Eng | Option_2_Eng | Option_3_Eng | Option_4_Eng | Ans | Vocab | Jpn | Option_1_Jpn | Option_2_Jpn | Option_3_Jpn | Option_4_Jpn | Exp | comment
1 | In the circuit shown in the figure, the combined resistance [ Ω ] between terminals a and b is | Picture_1 | 2.5 | 5 | 7.5 | 15 | 1 |  | {図}のような{回路}で、{端子}a - b間の{合成}抵抗[ Ω ]は。 | 2.5 | 5 | 7.5 | 15 | 5Ω×5Ω/5Ω+5Ω＝25/10=2.5 So, 5Ω+2.5Ω＝7.5Ω | 2017_1,
2 | In the AC circuit shown in the figure, when the power supply voltage is 204V, the voltage across the resistor is 180V, and the voltage across the reactance is 96V, the load power factor [ % ] is: | Picture_2 | 35 | 47 | 65 | 88 | 4 |  | {図}のような{交流}{回路}で、{電源}{電圧}204V、抵抗の{両端}の{電圧}が180V、リアクタンスの{両端}の{電圧}が96Vであるとき、{負荷}の{力率}[ % ]は。 | 35 | 47 | 65 | 88 | COSθ=Vr/V COSθ＝180/204＝0.88 so 0.88 x 100 = 88%. | 2017_1, 2016_2,
3 | There are two copper wires of the same material, A and B. A is 1.6mm in diameter and 20m in length, B is 3.2mm in diameter and 40m in length. How many times is the resistance of A greater than the resistance of B? |  | 2 | 3 | 4 | 5 | 1 |  | A、B 2本の同{材質}の{銅線}がある。Aは{直径}1.6mm、{長さ}20m、Bは{直径}3.2mm、{長さ}40mである。Aの抵抗はBの抵抗の何倍か。 | 2 | 3 | 4 | 5 | R=4×20/3.14×1.6×1.6=80/8.04=9.95Ω R=4×40/3.14×3.2×3.2=160/32.2=4.96Ω A is "twice" of the resistance of B. | 2017_1, 2015_1,
4 | In the AC circuit shown in the figure, a capacitor C was installed across the load to improve the power factor to 100%. What is the indicated value of the ammeter at this time? | Picture_4 | Become zero. | There is no change compared to before the capacitor was installed. | Increase compared to before installing the capacitor. | Reduced compared to before installation of the capacitor. | 4 |  | {図}のような{交流}{回路}で、{負荷}に対してコンデンサCを{設置}して、{力率}を100%に改善した。このときの{電流}計の{指示}{値}は。 | 零になる。 | コンデンサ{設置}前と比べて変化しない。 | コンデンサ{設置}前と比べて{増加}する。 | コンデンサ{設置}前と比べて{減少}する。 |  | 2017_1, 2015_1,
5 | In a 3-phase 3-wire 200V circuit as shown in the figure, the resistance between c and o was disconnected. What is the correct combination of voltage V [ V ] between a - o before disconnection and after disconnection? | Picture_5 | 116 before disconnection, 100 after disconnection | 116 before disconnection, 116 after disconnection | 100 before disconnection, 116 after disconnection | 100 before disconnection, 100 after disconnection | 1 |  | {図}のような{三相}3線式200Vの{回路}で、c - o間の抵抗が{断線}した。{断線}前と{断線}後のa - o間の{電圧}Vの{値}[ V ]{組合せ}として、{正しい}ものは。 | {断線}前116、{断線}後100 | {断線}前116、{断線}後116 | {断線}前100、{断線}後116 | {断線}前100、{断線}後100 | 200V=√3×phase voltage Phase voltage = 200v÷√3 = 200/1.73 = 115.6v The voltage across one resistor is 200/2=100V. Therefore, the voltage between a and o after disconnection is 100V. | 2017_1,
6 | As shown in the figure, the voltage across the load was 100V when power was supplied to a resistance load with a power consumption of 1500W through a wire length of 10m. What is the voltage drop [ V ] in the wiring? However, the electrical resistance of the wire shall be 5.0Ω per 1000m in length. | Picture_6 | 0.15 | 0.75 | 1.5 | 3 | 3 |  | {図}のように、{電線}のこう長10mの{配線}により、消費{電力}1500Wの抵抗{負荷}に{電力}を供給した{結果}、{負荷}の{両端}の{電圧}は100Vであった。{配線}における{電圧}降下[ V ]は。 ただし、{電線}の{電気}抵抗は{長さ}1000m{当たり}5.0Ωとする。 | 0.15 | 0.75 | 1.5 | 3 | P=VI. 1500w=100v×Ｉ Ｉ＝1500w÷100V Ｉ＝15A The resistance per 1m. 5Ω÷1000m＝0.005Ω 10m long wire is 0.0050×10=0.05Ω Voltage drop = 2 x I x r 2×15×0.05=1.5V. | 2018_2, 2018_1, 2017_1,
7 | When installing two 600V vinyl insulated wires (annealed copper wire) with a diameter of 2.0mm inside a pipe for low-voltage indoor wiring work using metal pipes, what is the allowable current [A] per wire? However, the ambient temperature should be 30°C or less, and the current reduction factor should be 0.7. |  | 19 | 24 | 27 | 35 | 2 |  | {金属}管による―{低圧}{屋内配線}{工事}で、{管内}に{直径}2.0mmの600Vビニル{絶縁}{電線}（ 軟{銅線} ）2本を収めて{施設}した{場合}、{電線}1本{当たり}の{許容}{電流}[ A ]は。 ただし、{周囲}{温度}は30℃{以下}、{電流}{減少}{係数}は0.7とする。 | 19 | 24 | 27 | 35 | The allowable current for a diameter of 2.0mm is 35A. So 35×0.7=24.5A | 2019_1, 2018_1, 2017_1, 2016_2, 2015_2,
8 | As shown in the figure, when a three-phase electric motor and heater are connected to a low-voltage indoor main line, what is the minimum current value [A] that determines the thickness of the main line? However, the demand rate is assumed to be 100%. | Picture_8 | 70 | 74 | 80 | 150 | 3 |  | {図}のように、{三相}の{電動機}と{電熱器}が{低圧}{屋内}{幹線}に{接続}されている{場合}、{幹線}の太さを決める{根拠}となる{電流}の{最小}{値}[ A ]は。 ただし、{需要}率は100%とする。 | 70 | 74 | 80 | 150 |  | 2017_1,
9 | In the design of branch circuits for low-voltage indoor wiring, what is inappropriate as a combination of circuit breakers for wiring, wire thickness of branch circuits, and outlets? However, the distance from the branch point to the circuit breaker for wiring is 3m, and the distance from the circuit breaker for wiring to the outlet is 8m. Also, the outlet shall not be a dual-purpose outlet. |  | 2 outlets with rated current of 15A | 2 outlets with rated current of 30A | 3 outlets with rated current of 20A | 1 outlet with rated current of 30A | 2 |  | {低圧}{屋内配線}の{分岐}{回路}の{設計}で、配線用{遮断器}、{分岐}{回路}の{電線}の太さ及び{コンセント}の{組み合わせ}として、{不適切}なものは。 ただし、{分岐}点から配線用{遮断器}までは3m、配線用{遮断器}から{コンセント}までは8mとし、{電線}の{数値}は{分岐}{回路}の{電線}（ 軟{銅線} ）に太さを{示す}。また、{コンセント}は{兼用}{コンセント}ではないものとする。 | Figure_9_A#{定格}{電流} 15Aの {コンセント}2個 | Figure_9_B#{定格}{電流} 30Aの {コンセント}2個 | Figure_9_C#{定格}{電流} 20Aの {コンセント}3個 | Figure_9_D#{定格}{電流} 30Aの {コンセント}1個 |  | 2019_1, 2018_1, 2017_1,
10 | As shown in the figure, connect the VVR cable thickness 8 mm from the low-voltage indoor main line protected by the wiring breaker with a rated current of 50 A. 2 When branching a low-voltage indoor electric circuit with (allowable current 42A), what is the maximum length between a and b [m]? However, the load connected to the low-voltage indoor trunk line shall be the lighting load. | Picture_10 | 3 | 5 | 8 | No limit | 4 |  | {図}のように{定格}{電流}50Aの{配線}用{遮断器}で保護された{低圧}{屋内}{幹線}からVVRケーブル太さ8mm2（ {許容}{電流}42A ）で{低圧}{屋内}{電路}を{分岐}する{場合}、a-b間の{長さ}の{最大値}[ m ]は。 ただし、{低圧}{屋内}{幹線}に{接続}される{負荷}は、{電灯}{負荷}とする。 | 3 | 5 | 8 | {制限}なし |  | 2017_1,
11 | What is the main purpose of using insulating bushings in metal pipe work? |  | To prevent damage to the wire coating. | For connecting metal pipes to each other. | For fixing metal pipes to building materials. | To facilitate the connection of electric wires. | 1 |  | {金属}{管}{工事}において、{絶縁}ブッシングを{使用}する主な{目的}は。 | {電線}の{被覆}を{損傷}させないため。 | {金属}{管}{相互}を{接続}するため。 | {金属}{管}を造営材に固定するため。 | {電線}の{接続}を{容易}にするため。 |  | 2017_1,
12 | Compared to incandescent lamps, what are the characteristics of self-ballasted LED lamps (with a built-in controller) that are incorrect? |  | short lifespan. | High luminous efficiency (less power consumption at the same brightness). | Price is high. | Low power factor. | 1 |  | {白熱電球}と{比較}して、電球形LEDランプ（ 制御装置内蔵型 ）の特徴として、誤っているものは。 | 寿命が短い。 | 発光効率が{高い}（ {同じ}明るさでは消費{電力}が少ない ）。 | 価格が{高い}。 | {力率}が低い。 |  | 2018_1, 2017_2, 2017_1,
13 | What is wrong in the description about general-purpose low-voltage three-phase squirrel-cage induction motors? |  | The starting current for a direct-on-line (full-voltage) start is about 4 to 8 times the full-load current. | As the load increases, the rotation speed decreases slightly. | Rotational speed increases when the frequency of the power supply changes from 60Hz to 50Hz. | Reversing any two of the three connections will reverse the rotation. | 3 |  | 一般用{低圧}{三相}かご形{誘導電動機}に関する{記述}で誤っているものは。 | じか入れ（ 全{電圧} ）{始動}での{始動}{電流}は全{負荷}{電流}の4～8倍{程度}である。 | {負荷}が{増加}すると{回転}{速度}がやや低下する。 | {電源}の{周波数}が60Hzから50Hzに変わると{回転}{速度}が{増加}する。 | 3本の結{線}のうちいずれか2本を入れ替えると逆{回転}する。 |  | 2017_1,
14 | What is the appropriate combination of materials and tools for attaching metal pipes to concrete walls? |  | Horso, Curl Plug, Hammer, Stable | Vibration drill, curl plug, saddle, wood screw | Hammer, chisel, stable, concrete nail | vibration drill, horso, saddle, bolt | 2 |  | コンクリート{壁}に{金属}{管}を取り付けるときに用いる{材料}及び{工具}の{組み合わせ}として、{適切}のものは。 | ホルソ、カール{プラグ}、ハンマ、ステーブル | {振動}ドリル、カール{プラグ}、サドル、木ねじ | ハンマ、たがね、ステーブル、コンクリート釘 | {振動}ドリル、ホルソ、サドル、ボルト |  | 2017_1,
15 | What devices are used in grid-connected photovoltaic power generation facilities? |  | power conditioner | low voltage phase advance capacitor | Light modulator | automatic flasher | 1 |  | 系統連系型の太陽{電池}{発電}{設備}において{使用}される{機器}は。 | パワーコンディショナ | {低圧}進相コンデンサ | {調光器} | {自動}{点滅器} |  | 2019_1, 2018_2, 2017_1,
16 | What is the purpose of the tool shown in the photo? | Picture_16 | Used for cutting metal pipes. | Used for cutting lighting ducts. | Used for cutting hard vinyl chloride conduit. | Used for cutting metal wire. | 3 |  | {写真}に{示す}{工具}の{用途}は。 | {金属}{管}の{切断}に{使用}する。 | ライティングダクトの{切断}に{使用}する。 | {硬質}塩化ビニル{電線}{管}の{切断}に{使用}する。 | {金属}{線}ぴの{切断}に{使用}する。 |  | 2017_1,
17 | What is the name of the instrument shown in the photo? | Picture_17 | Leakage alarm | Electromagnetic switch | earth leakage breaker | Wiring circuit breaker (also used for motor protection) | 4 |  | {写真}に{示す}{器具}の{名称}は。 | {漏電}{警報器} | {電磁}{開閉器} | {漏電}{遮断器} | {配線}用{遮断器}（ {電動機}保護{兼用} ） |  | 2017_1,
18 | What is the name of the measuring instrument shown in the photo? | Picture_18 | Phaser | frequency meter | clamp type ammeter | Illuminometer | 4 |  | {写真}に{示す}{測定}器の{名称}は。 | 検相器 | {周波数}計 | クランプ形{電流}計 | {照度}計 |  | 2017_1,
19 | Inappropriate combination of special place and low-voltage indoor wiring work to be constructed in that place. |  | Places with combustible gas where propane gas is subdivided into other small containers --- Cable work using MI cable | Locations where hazardous materials that store petroleum exist ----------------------------- Do not put 600V vinyl-insulated vinyl-sheathed cables in protective devices. Cable work used in | Locations with combustible dust for sifting flour ------------------- Synthetic resin piping work using hard vinyl chloride conduit VE28 | Locations with flammable gas for spray painting work in automobile repair shops ----- Metal pipe work using thick steel conduits | 2 |  | 特殊{場所}とその{場所}に{施工}する{低圧}{屋内配線}{工事}の{組み合わせ}で、{不適切}なものは。 | プロパンガスを他の小さな容器に小分けする可燃性ガスのある{場所} --- MIケーブルを{使用}したケーブル{工事} | 石油を貯蔵する{危険}{物の}存在する{場所} ----------------------------- 600Vビニル{絶縁}ビニルシースケーブルを{防護}装置に収めないで{使用}したケーブル{工事} | 小麦粉をふるい分けする可燃性粉じんのある{場所} ------------------- {硬質}塩化ビニル{電線}{管}VE28を{使用}した{合成}樹脂{管}{工事} | {自動}車修理{工場}の吹き付け塗装{作業}を行う可燃性ガスのある{場所} ----- 厚鋼{電線}{管}を{使用}した{金属}{管}{工事} |  | 2017_1, 2015_2,
20 | We constructed a single-phase 3-wire 100/200V residential distribution board for indoor wiring. inappropriate ones. |  | A 2-pole 2-element circuit breaker was installed in the branch circuit of the room air conditioner (single-phase 200 V). | A 2-pole 2-element circuit breaker was attached to the branch circuit of the electric heater (single-phase 100 V). | A copper bar was attached to the neutral pole of the main switch. | A 2-pole, 1-element circuit breaker was attached to the branch circuit dedicated to lighting (single-phase 100 V), and the neutral wire was connected to the pole with the element. | 4 |  | {単相}3線式100／200V{屋内配線}の{住宅}用{分電盤}の{工事}を{施工}した。{不適切}なものは。 | ルームエアコン（ {単相}200V ）の{分岐}{回路}に2{極}2素子の{配線}用{遮断器}を取り付けた。 | {電熱器}（ {単相}100V ）の{分岐}{回路}に2{極}2素子の{配線}用{遮断器}を取り付けた。 | 主{開閉器}の中性{極}に銅バーを取り付けた。 | {電灯}{専用}（ {単相}100V ）の{分岐}{回路}に2{極}1素子の{配線}用{遮断器}を取り付け、素子のある{極}に中性線を{結線}した。 |  | 2017_1, 2016_2,
21 | What are inappropriate types of construction work at indoor wiring facilities with a working voltage of 100V? |  | Metal pipe work in a dry place that cannot be inspected | Synthetic resin pipe work in a highly humid location where inspection is not possible (excluding CD pipes) | Cable work in unfolded and damp locations | Lighting duct work in an open area with high humidity | 4 |  | {使用}{電圧}100Vの{屋内配線}の{施設}{場所}における{工事}の{種類}で、{不適切}なものは。 | {点検}できない隠ぺい{場所}であって、乾燥した{場所}の{金属}{管}{工事} | {点検}できない隠ぺい{場所}であって、{湿気}の多い{場所}の{合成}樹脂{管}{工事}（ CD{管}を除く ） | 展開した{場所}であって、{湿気}の多い{場所}のケーブル{工事} | 展開した{場所}であって、{湿気}の多い{場所}のライティングダクト{工事} |  | 2019_2, 2017_1, 2015_1,
22 | What is inappropriate as construction work for the low-voltage house side wiring part to supply electricity with a working voltage of 100V to the garage on the same site? |  | Cable construction using 600V cross-linked polyethylene insulated vinyl sheath cable (CV) | Synthetic resin pipe construction using hard vinyl chloride conduit (VE) | Metal wire work using Type 1 metal wire | Cable construction using 600V vinyl-insulated vinyl-sheathed round cable (VVR) | 3 |  | 同一敷地内の車庫へ{使用}{電圧}100Vの{電気}を供給するための{低圧}屋側{配線}{部分}の{工事}として、{不適切}なものは。 | 600V{架橋}ポリエチレン{絶縁}ビニルシースケーブル（ CV ）によるケーブル{工事} | {硬質}塩化ビニル{電線}{管}（ VE ）による{合成}樹脂{管}{工事} | 1{種}{金属}製{線}ぴによる{金属}{線}ぴ{工事} | 600Vビニル{絶縁}ビニルシースケーブル丸形（ VVR ）によるケーブル{工事} |  | 2017_1,
23 | What is inappropriate as a construction method for Class D grounding work? |  | An annealed copper wire with a diameter of 1.6 mm was used as the ground wire for the room air conditioner. | A single-phase 100V electric motor was installed in a damp location, and a current-operated ground fault circuit breaker with a rated sensitivity current of 30mA and an operation time of 0.1 seconds was installed, eliminating grounding work. | A device was installed to automatically cut off the electric circuit within 0.5 seconds when a ground fault occurred in the low voltage circuit, and the ground resistance value was 300Ω. | Multi-core cabtyre cable cross-sectional area of ​​0.75 mm as a ground wire for the metal outer casing of electrical equipment that is used while moving. 2 1 heart was used. | 2 |  | D{種}{接地}{工事}の{施工}{方法}として、{不適切}なものは。 | ルームエアコンの{接地}線として、{直径}1.6mmの軟{銅線}を{使用}した。 | {単相}100Vの{電動機}を{水気}のある{場所}に{設置}し、{定格}{感度}{電流}30mA、{動作時間}0.1秒の{電流}作動型{漏電}{遮断器}を取り付けたので、{接地}{工事}を{省略}した。 | {低圧}{電路}に地絡を生じた{場合}に0.5秒以内に{自動}的に{電路}を{遮断}する装置を{設置}し、{接地}抵抗{値}が300Ωであった。 | 移動して{使用}する{電気}{機械}{器具}の{金属}製{外箱}の{接地}{線}として、多心キャプタイヤケーブルの{断面積}0.75mm2の1心を{使用}した。 |  | 2018_2, 2017_1,
24 | What is the wrong combination of measuring instruments used in low-voltage circuits and their applications? |  | Clamp-type ammeter and load current measurement | Circuit meter (tester) and continuity check | Phase detector and motor rotation speed measurement | Voltage detector and confirmation of electric circuit charge | 3 |  | {低圧}{電路}で{使用}する{測定}器とその{用途}の{組み合わせ}として、誤っているものは。 | クランプ形{電流}計 と {負荷}{電流}の{測定} | {回路}計（ テスタ ） と {導通}の{確認} | 検相器 と {電動機}の{回転}{速度}の{測定} | {検電器} と {電路}の{充電}の有無の{確認} |  | 2017_2, 2017_1,
25 | I wanted to measure the insulation resistance of low-voltage indoor wiring, but it was difficult to measure it when the electric circuit was cut off, so I checked the insulation performance by measuring the leakage current. What is the maximum value [mA] of leakage current that can be judged to have the insulation performance specified in the "Interpretation of Technical Standards for Electrical Equipment"? |  | 0.1 | 0.2 | 1 | 2 | 3 |  | {低圧}{屋内配線}の{絶縁}抵抗{測定}を行いたいが、その{電路}を停電して{測定}することが困難なため、漏えい{電流}により{絶縁}{性能}を{確認}した。「{電気}{設備}の{技術基準}の{解釈}」に定める{絶縁}{性能}を有していると{判断}できる漏えい{電流}の{最大値}[ mA ]は。 | 0.1 | 0.2 | 1 | 2 |  | 2019_1, 2017_1,
26 | What is wrong about earth resistance meter (battery type)? |  | Before measuring the ground resistance, confirm that the battery capacity of the ground resistance meter is normal. | Before measuring the earth resistance, open the terminals and adjust the zero point of the indicator. | Before measuring the earth resistance, confirm that the earth voltage of the earth is below the allowable value. | Prior to ground resistance measurement, it is necessary to place the auxiliary pole in the proper position. | 2 |  | {接地}抵抗計（ {電池}式 ）に関する{記述}として、誤っているものは。 | {接地}抵抗{測定}の前には、{接地}抵抗計の{電池}{容量}が正常であることを{確認}する。 | {接地}抵抗{測定}の前には、{端子}間を{開放}して{測定}し、{指示}計の零点の調整をする。 | {接地}抵抗{測定}の前には、{接地}の地{電圧}が{許容}{値}{以下}であることを{確認}する。 | {接地}抵抗{測定}の前には、{補助}{極}を適正な{位置}に{配置}することが{必要}である。 |  | 2017_1, 2015_1,
27 | The AC circuit in the figure is a circuit that measures the voltage, current, and power of the load. What is the correct combination of instruments indicated by a, b, and c in the part? | Picture_27 | a. Ammeter, b. Voltmeter, c. Wattmeter | a. Wattmeter, b. Ammeter, c. Voltmeter | a. Voltmeter, b. Ammeter, c. Wattmeter | a. Voltmeter, b. Wattmeter, c. Ammeter | 3 |  | {図}の{交流}{回路}は、{負荷}の{電圧}、{電流}、{電力}を{測定}する{回路}である。部中にa、b、cで{示す}{計器}の{組み合わせ}として、{正しい}ものは。 | a. {電流}計、b. {電圧}計、c. {電力}計 | a. {電力}計、b. {電流}計、c. {電圧}計 | a. {電圧}計、b. {電流}計、c. {電力}計 | a. {電圧}計、b. {電力}計、c. {電流}計 |  | 2019_2, 2017_1,
28 | Anything that violates the Electrician Law. |  | Although he passed the electrician's examination, he did not apply for a license from the prefectural governor because he did not engage in electrical work. | In order not to lose the electrician's license, the electrician engaged in electric work while keeping it in the office. | An electrician changed his address, but did not notify the prefectural governor of this within 30 days. | An electrician engaged in electrical work in multiple prefectures without notifying the Minister of Economy, Trade and Industry. | 2 |  | {電気}{工事}士法に違反しているものは。 | {電気}{工事}士試験に合格したが、{電気}{工事}の{作業}に{従事}しないので都{道}府県知事に{免状}の交付申請をしなかった。 | {電気}{工事}士が{電気}{工事}士{免状}を紛失しないよう、これを営業所に保{管}したまま{電気}{工事}に{従事}した。 | {電気}{工事}士が{住所}を変更したが、30日以内に都{道}府県知事にこれを届け出なかった。 | {電気}{工事}士が経済産業大臣に届け出をしないで、複数の都{道}府県で{電気}{工事}の{作業}に{従事}した。 |  | 2017_1,
29 | According to the Electrician Law, in the construction work related to general electric facilities, both a and b cannot be engaged unless they are an electrician. |  | a: Attach the switchboard to the construction material. b: Bend the conduit. | a: Install pipes for underground cables. b: Install a power meter with a rated voltage of 240V. | a: Install poles to support the wires. b: Put the wire in the conduit. | a: Bury the ground electrode in the ground. b: Connect the cord to a plug-in connector with a rated voltage of 125V. | 1 |  | {電気}{工事}士法において、一般用{電気}工{作物}に係る{工事}{作業}でa、bともに{電気}{工事}士ではければ{従事}できないものは。 | a: {配電盤}を造営材に取り付ける。 b: {電線}{管}を曲げる。 | a: {地中}{電線}用の{管}を{設置}する。 b: {定格}{電圧}240Vの{電力}量計を取り付ける。 | a: {電線}を支持する柱を{設置}する。 b: {電線}{管}に{電線}を収める。 | a: {接地}{極}を地面に埋没する。 b: {定格}{電圧}125Vの差し込み{接続}器にコー |  | 2017_1, 2015_1,
30 | Among the following wiring devices used for low-voltage indoor electric circuits, those subject to the application of specific electrical appliances. However, the rated voltage, rated current, location of use, structure, etc. shall all fall under the category of electrical appliances stipulated in the "Electrical Appliance and Material Safety Law." |  | Knife switch with cover | Electromagnetic switch | lighting duct | time switch | 4 |  | {低圧}の{屋内}{電路}に{使用}する次の{配線}{器具}のうち、{特定}{電気}{用品}の{適用}を受けるものは。 ただし、{定格}{電圧}、{定格}{電流}、{使用}{箇所}、{構造}等すべて「{電気}{用品}安全法」に定める{電気}{用品}に該当するものとする。 | カバー付きナイフ{スイッチ} | {電磁}{開閉器} | ライティングダクト | タイム{スイッチ} |  | 2018_2, 2017_1, 2016_1,
31 | What is the symbol for the distribution board installed in the part indicated by ①? |  | Picture_31_A | Picture_31_B | Picture_31_C | Picture_31_D | 3 |  | ①で{示す}{部分}に取り付ける{分電盤}の{図}{記号}は。 | Picture_31_A | Picture_31_B | Picture_31_C | Picture_31_D |  | 2017_1,
32 | What type of pipe is used for the wiring work of the part indicated by ②? |  | wave pay hard synthetic resin tube | Rigid PVC Conduit | Impact-resistant hard vinyl chloride conduit | Synthetic resin flexible conduit | 4 |  | ②で{示す}{部分}の{配線}{工事}で用いる{管}の{種類}は。 | 波付{硬質}{合成}樹脂{管} | {硬質}塩化ビニル{電線}{管} | 耐衝撃性{硬質}塩化ビニル{電線}{管} | {合成}樹脂製可とう{電線}{管} |  | 2017_1,
33 | The outdoor light indicated by ③ is a 100W mercury lamp. What is the correct sidenote for the graphic symbol? |  | N100 | H100 | M100 | W100 | 2 |  | ③で{示す}外灯は、100Wの{水銀灯}である。その{図}{記号}の傍記{表示}として、{正しい}ものは。 | N100 | H100 | M100 | W100 |  | 2017_1,
34 | What is the name of the symbol shown in ④? |  | emergency lighting | general lighting | induction lights | Security Lighting | 3 |  | ④で{示す}{図}{記号}の{名称}は。 | 非常用照明 | 一般用照明 | {誘導}灯 | {保安}用照明 |  | 2017_1,
35 | Equipment with the symbol shown in ⑤. |  | Buzzer for overload warning | Push button for electromagnetic switch with confirmation display | Blue pilot lamp that lights up when driving | Float switch for driving load | 2 |  | ⑤で{示す}{図}{記号}の{器具}は。 | {過負荷}警報を知らせるブザー | {確認}{表示}付の{電磁}{開閉器}用押しボタン | 運転時に{点灯}する青色のパイロットランプ | {負荷}を運転させるためのフロート{スイッチ} |  | 2017_1,
| What is the name of the symbol shown in ⑥? |  | power meter | time switch | circuit breaker for wiring | power meter | 4 |  | ⑥で{示す}{図}{記号}の{名称}は。 | {電力}計 | タイム{スイッチ} | {配線}用{遮断器} | {電力}量計 |  | 2017_1,
37 | What is the minimum allowable value [MΩ] for the insulation resistance between the electric circuit and the ground in the part indicated by ⑦? |  | 0.1 | 0.2 | 0.4 | 1 | 2 |  | ⑦で{示す}{部分}の{電路}と{大地}間の{絶縁}抵抗として、{許容}される{最小}{値}[ MΩ ]は。 | 0.1 | 0.2 | 0.4 | 1 |  | 2017_1,
38 | What is the minimum number of wires (number of cores) for the part indicated by ⑧? |  | 2 | 3 | 4 | 5 | 1 |  | ⑧で{示す}{部分}の{最小}{電線}{本数}（心線数）は。 | 2 | 3 | 4 | 5 |  | 2017_1,
39 | The part indicated by ⑨ is a hook-type outlet. What is the correct sidenote notation for the graphic symbol? |  | T | ET | EL | LK | 1 |  | ⑨で{示す}{部分}は引掛形の{コンセント}である。その{図}{記号}の傍記表記として、{正しい}ものは。 | T | ET | EL | LK |  | 2018_1, 2017_1,
40 | What is the minimum height [m] above the ground surface of the spur line attachment point indicated by ⑩? However, the service line shall not cross the road, be technically unavoidable, and shall not hinder traffic. |  | 2.5 | 3 | 3.5 | 4 | 1 |  | ⑩で{示す}引込{線}取付点の地表上の{高さ}の最低{値}[ m ]は。 ただし、引込{線}は{道}路を横断せず、技術上やむを得ない{場合}で、交通に支障がないものとする。 | 2.5 | 3 | 3.5 | 4 |  | 2017_1, 2016_2,
41 | The symbol shown in ⑪ is |  | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D | 3 |  | ⑪で{示す}{図}{記号}は。 | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D |  | 2017_1, 2015_2,
42 | In the ceiling of the part indicated by ⑫, what is the correct combination of the type and number of ring sleeves and the stamp after connection when the connection work is crimped with a ring sleeve? However, all wires used shall be VVF1.6. Also, the "○", "Small", and "Medium" in the center of the ring sleeve shown in the photo represent the markings after connection. |  | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D | 4 |  | ⑫で{示す}{部分}の{天井}内において、{接続}{工事}をリングスリーブで{圧着}{接続}した{場合}のリングスリーブの{種類}、{個数}及び{接続}後の{刻印}との{組み合わせ}で{正しい}ものは。 ただし、{使用}する{電線}はすべてVVF1.6とする。 また、{写真}に{示す}リングスリーブ{中央}の「〇」、「小」、「中」は{接続}後の{刻印}を表す | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D |  | 2017_1,
43 | In part ⑬, what is the appropriate tool for crimping and connecting the crimp terminal shown in the photo below and the ground wire? | Picture_43 | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D | 4 |  | ⑬の{部分}で、下の{写真}に{示す}{圧着}{端子}と{接地}{線}を{圧着}{接続}するための{工具}として、{適切}なものは。 | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D |  | 2018_2, 2017_1,
44 | ⑭ What is the equipment with the symbol shown in ⑭? |  | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D | 1 |  | ⑭で{示す}{図}{記号}の{器具}は。 | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D |  | 2017_1,
45 | The one with the symbol shown in ⑮. |  | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D | 2 |  | ⑮で{示す}{図}{記号}のものは。 | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D |  | 2017_1,
46 | Those that are not used in the construction of the part shown in ⑯. |  | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D | 1 |  | ⑯で{示す}{部分}の{工事}において{使用}されることのないものは。 | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D |  | 2017_1, 2016_2,
47 | If all the connections in the joint box for VVF shown in (17) are plug-in connectors, what is the appropriate combination of plug-in connector type and minimum number to be used? However, all electric wires used shall be VVF1.6, and the number of electric wires (number of core wires) for wiring to the first basement floor shall be minimized. |  | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D | 3 |  | ⑰で{示す}VVF用ジョイントボックス内の{接続}をすべて差込型{コネクタ}とする{場合}、{使用}する差込型{コネクタ}の{種類}と{最少}{個数}の{組み合わせ}で、{適切}なものは。 ただし、{使用}する{電線}はすべてVVF1.6とし、地下1階に至る{配線}の{電線}{本数}（心線数）は{最小}とする | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D |  | 2017_1,
48 | If all the connections in the joint box for VVF shown in ⑱ are crimped connections, what is the appropriate combination of the type and minimum number of ring sleeves to be used? However, all wires used shall be VVF1.6. |  | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D | 2 |  | ⑱で{示す}VVF用ジョイントボックス内の{接続}をすべて{圧着}{接続}とする{場合}、{使用}するリングスリーブの{種類}と{最少}{個数}の{組み合わせ}で、{適切}なものは。 ただし、{使用}する{電線}はすべてVVF1.6とする。 | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D |  | 2017_1,
49 | The equipment with the symbol shown in ⑲. |  | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D | 2 |  | ⑲で{示す}{図}{記号}の{器具}は。 | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D |  | 2017_1, 2015_2,
50 | In this wiring diagram, which switch is not used? However, the diagram below the photo shows the configuration of the contacts. |  | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D | 4 |  | この{配線}{図}で、{使用}されていない{スイッチ}は。 ただし、{写真}下の{図}は、{接点}の{構成}を{示す}。 | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D |  | 2017_1,