## Sheet1
no | Eng | Picture | Option_1_Eng | Option_2_Eng | Option_3_Eng | Option_4_Eng | Ans | Vocab | Jpn | Option_1_Jpn | Option_2_Jpn | Option_3_Jpn | Option_4_Jpn | Exp | comment
1 | In the circuit shown in the figure, the combined resistance [Ω] between terminals a and b is. | Picture_1 | 1 | 2 | 3 | 4 | 2 | ['回路(かいろ)-Circuit', '端子(たんし)-Port', '合成(ごうせい)- Combining', '抵抗(ていこう)- resistance'] | {図}のような{回路}で、{端子}a - b間の{合成}抵抗［Ω］は。 | 1 | 2 | 3 | 4 | 2Ω. 2×2/(2+2)=1(Ω) 3×6/(3+6)=2(Ω) 1+2=3(Ω) so 3×6/(3+6)=2(Ω) | 2018_2, 2016_1, 2017_1,
2 | In the AC circuit as shown in the figure, the voltage V [V] across the resistance 12Ω is. | Picture_2 | 86 | 114 | 120 | 160 | 3 | ['抵抗(ていこう)- Resistance', '回路(かいろ)- Circuit'] | {図}のような{交流}{回路}において、抵抗12Ωの{両端}の{電圧}V［V］は。 | 86 | 114 | 120 | 160 | Z=√(R2+XL2), so Z=√(12×12+16×16) =20(Ω) And I = V/Z = 200/20 = 10[A] R×I = 12×10 = 120[V] | 2019_1, 2018_2, 2017_2, 2016_1,
3 | What is the copper conductor of the same material that has the closest resistance to the copper conductor with a diameter of 2.6 mm and a length of 10 m? |  | Diameter 1.6mm, length 20m | Cross- sectional area 8mm 2 , length 10m | Diameter 3.2mm, length 5m | Cross- sectional area 5.5mm 2 , length 10m | 4 | ['導線(どうせん)－Conducting wire', '長さ(なが)- Length', '直径(ちょっけい)- Diameter'] | {直径}2.6mm、{長さ}10mの銅{導線}と抵抗{値}が最も近い同{材質}の銅{導線}は。 | {直径}1.6mm、{長さ}20m | {断面積}8mm2、{長さ}10m | {直径}3.2mm、{長さ}5m | {断面積}5.5mm2、{長さ}10m | 4 conducting wire has almost the same cross-sectional area and length as the prepared conducting wire. | 2019_2, 2018_2, 2016_2,
4 | What is the amount of electric power [kW ・ h] required to raise the temperature of 60 kg of water by 20 K using an electric heater? However, the specific heat of water shall be 4.2 kJ / (kg · K) and the thermal efficiency shall be 100%. |  | 1.0 | 1.2 | 1.4 | 1.6 | 3 | ['熱効率(ねつこうりつ)- Thermal efficiency', '比熱(ひねつ)- Specific heat', '電力量(でんりょくりょう)-Electric energy', '温度(おんど)- Temperature', '電熱器(でんねつき)-Electrothermic equipment'] | {電熱器}により、60kgの水の{温度}を20K上昇させるのに{必要}な{電力}量［kW・h］は。ただし、水の{比熱}は4.2kJ／（kg・K）とし、{熱効率}は100%とする。 | 1.0 | 1.2 | 1.4 | 1.6 | 60×20×4.2=5040KJ W=5040/3600=1.4KW·h. | 2019_1, 2018_2, 2015_2,
5 | What is the current I [A] flowing through the three-phase three-wire circuit as shown in the figure? | Picture_5 | 8.3 | 11.6 | 14.3 | 20.0 | 2 | ['電流(でんりゅう)- Electric current', '回路(かいろ)- Circuit', '三相(さんそう)-Three phases'] | {図}のような{三相}３{線}式{回路}に{流れる}{電流}I［A］は。 | 8.3 | 11.6 | 14.3 | 20.0 |  | 2019_2, 2018_2, 2015_2,
6 | As shown in the figure, as a result of supplying power to a resistance load having a power consumption of 2000 W by wiring with a length of 8 m, the voltage across the load was 100 V. What is the voltage drop [V] in the wiring? However, the electrical resistance of the wire shall be 3.2Ω per 1000m in length. | Picture_6 | 1 | 2 | 3 | 4 | 1 | ['両端(りょうたん)-Both ends', '負荷(ふか)- load (electrical)', '結果(けっか)- Result', '抵抗(ていこう)- Resistance', '消費電力(しょうひでんりょく)-Electricity consumption Electricity consumption', '配線(はいせん)- wiring'] | {図}のように、{電線}のこう長８mの{配線}により、消費{電力}2000Wの抵抗{負荷}に{電力}を供給した{結果}、{負荷}の{両端}の{電圧}は100Vであった。{配線}における{電圧}降下［V］は。ただし、{電線}の{電気}抵抗は{長さ}1000m{当たり}3.2Ωとする。 | 1 | 2 | 3 | 4 | I [A] = 2000 / 100 = 20 [A] the voltage drop is 2 lines (8 x 2 m) so, 16 x 3.2 / 1000 = 0.0512 [Ω] 0.0512 [Ω ] × 20 [A] ≒ 1 [V] | 2018_2, 2018_1, 2017_1,
7 | In a single-phase three-wire circuit as shown in the figure, when the resistance per wire is 0.1Ω, the voltage [V] between a and b is. | Picture_7 | 102 | 103 | 104 | 105 | 3 | ['電線(でんせん)-Electric cable', '回路(かいろ)- Circuit', '単相(たんそう)- Single Phase'] | {図}のような{単相}３線式{回路}において、{電線}１線{当たり}の抵抗が0.1Ωのとき、a - b間の{電圧}［V］は。 | 102 | 103 | 104 | 105 | The voltage drop here is 0.1[Ω]×10[A]=1[V] So, 105-1=104[V] | 2018_1, 2018_2, 2016_1,
8 | 600V vinyl insulated vinyl sheath cable used for low pressure indoor wiring work Round shape (copper conductor), conductor diameter 2.0mm, allowable current [A] for 3 cores. However, the ambient temperature shall be 30 ° C or less, and the current reduction coefficient shall be 0.70. |  | 19 | 24 | 33 | 35 | 2 | ['許容(きょよう)- Permission', '導体(どうたい)- Conductor', '円形(えんけい)- Round shape', '絶縁(ぜつえん)-Insulation', '低圧(ていあつ)-Low pressure'] | {低圧}{屋内配線}{工事}に{使用}する600Vビニル{絶縁}ビニルシースケーブル丸形（銅{導体}）、{導体}の{直径}2.0mm、３心の{許容}{電流}［A］は。ただし、{周囲}{温度}は30°C{以下}、{電流}{減少}{係数}は0.70とする。 | 19 | 24 | 33 | 35 | The allowable current for a wire with a diameter of 2.0mm is 35A. So, 35×0.7=24.5[A] | 2018_2,
9 | When branching from a low-voltage indoor trunk line protected by an overcurrent circuit breaker with a rated current of 125 A as shown in the figure and installing an overcurrent circuit breaker at a position of 10 m, the minimum allowable current of the wire between a and b [ A] is. | Picture_9 | 44 | 57 | 69 | 89 | 3 | ['分岐(ぶんき)-Divergence', '屋内(おくない)-Indoor', '遮断器(しゃだんき)- Circuit breaker', '過電流(かでんりゅう)- Excess current', '定格(ていかく)- Rated value'] | {図}のように{定格}{電流}125Aの過{電流}{遮断器}で保護された{低圧}{屋内}{幹線}から{分岐}して、10mの{位置}に過{電流}{遮断器}を{施設}するとき、a - b間の{電線}の{許容}{電流}の{最小}{値}［A］は。 | 44 | 57 | 69 | 89 | If the distance from the branch point to the overcurrent breaker at the branch destination exceeds 8m, the value of the overcurrent breaker of the breaker × 0.55 will be the allowable current of the wire between a and b. Therefore, 125×0.55=68.75[A] | 2019_2, 2019_1, 2018_1, 2018_2, 2016_2, 2016_1, 2015_1, 2015_2,
10 | What is the appropriate combination of a circuit breaker for wiring, the thickness of the wire of the branch circuit, and the outlet in the design of the branch circuit for low-voltage indoor wiring? However, the distance from the branch point to the molded case circuit breaker is 3 m, the distance from the molded case circuit breaker to the outlet is 8 m, and the numerical value of the electric wire indicates the thickness of the electric wire (annealed copper wire) of the branch circuit. In addition, the outlet shall not be a dual-purpose outlet. |  | 2 outlets with rated current of 20A | 2 outlets with rated current of 20A | 1 outlet with rated current of 30A | 1 outlet with rated current of 15A | 1 | ['兼用(けんよう)- Multi-use', '銅線(どうせん)- Copper line', '分岐(ぶんき)- Divergence', '数値(すうち)- Numerical value', '配線用遮断器(はいせんようしゃだんき)- Molded-case circuit breaker; MCCB', '分岐点(ぶんきてん)- ', '組み合わせ(くみあわせ)- Combination'] | {低圧}{屋内配線}の{分岐}{回路}の{設計}で、配線用{遮断器}、{分岐}{回路}の{電線}の太さ及び{コンセント}の{組合せ}として、{適切}なものは。ただし、{分岐}点から配線用{遮断器}までは３m、配線用{遮断器}から{コンセント}までは８mとし、{電線}の{数値}は{分岐}{回路}の{電線}（軟{銅線}）の太さを{示す}。また、{コンセント}は{兼用}{コンセント}ではないものとする。 | Figure_10_A#{定格}{電流} 20Aの {コンセント}2個 | Figure_10_B#{定格}{電流} 20Aの {コンセント}2個 | Figure_10_C#{定格}{電流} 30Aの {コンセント}1個 | Figure_10_D#{定格}{電流} 15Aの {コンセント}1個 |  | 2018_2,
11 | What is wrong with the description of the earth-leakage circuit breaker? |  | The high-speed type earth-leakage circuit breaker has an operating time of 0.1 seconds or less at the rated sensitivity current. | The earth-leakage circuit breaker detects the ground fault current with a zero-phase current transformer. | The high-sensitivity type earth-leakage circuit breaker has a rated sensitivity current of 1000 mA or less. | The earth-leakage circuit breaker has a test device that simulates an earth-leakage current. | 3 | ['兼用(けんよう)- Multi-use', '分岐(ぶんき)- Divergence', '分岐点(ぶんきてん)- Junction', '太い(ふとい)-Fat'] | {漏電}{遮断器}に関する{記述}として、誤っているものは。 | 高速形{漏電}{遮断器}は、{定格}{感度}{電流}における{動作時間}が0.1秒{以下}である。 | {漏電}{遮断器}は、零相{変流器}によって地絡{電流}を{検出}する。 | 高{感度}形{漏電}{遮断器}は、{定格}{感度}{電流}が1000mA{以下}である。 | {漏電}{遮断器}には、{漏電}{電流}を模擬したテスト装置がある。 |  | 2018_2, 2016_2,
12 | What can be used when low-voltage underground wiring is directly buried? |  | 600V cross-linked polyethylene insulated vinyl sheath cable (CV) | 600V vinyl insulated wire (IV) | Vinyl insulated wire for lead-in (DV) | Outdoor vinyl insulated wire (OW) | 1 | ['架橋(かきょう)- Cross-link', '地中(ちちゅう)- Underground'] | {低圧}の{地中}{配線}を{直接}埋設式により{施設}する{場合}に{使用}できるものは。 | 600V{架橋}ポリエチレン{絶縁}ビニルシースケーブル（CV） | 600Vビニル{絶縁}{電線}（IV） | 引込用ビニル{絶縁}{電線}（DV） | {屋外}用ビニル{絶縁}{電線}（OW） |  | 2018_2,
13 | When using a three-phase squirrel-cage induction motor with 6 poles at a frequency of 50 Hz, the closest rotation speed [min -1 ] is. |  | 500 | 1000 | 1500 | 3000 | 2 | ['周波数(しゅうはすう)- Frequency', '誘導電動機(ゆうどうでんどうき)- Induction motor', '極(きょく)- Pole'] | {極}数６の{三相}かご形{誘導電動機}を{周波数}50Hzで{使用}するとき、最も近い{回転}{速度}［min-1］は。 | 500 | 1000 | 1500 | 3000 |  | 2019_1, 2018_2, 2018_1, 2015_2,
14 | What is the appropriate combination of the type of electrical work and the tools used in that work? |  | Bus duct construction and gas torch lamp | Synthetic resin pipe construction and pipe bender | Metal wire construction and bolt clipper | Metal pipe construction and reamer | 4 | ['工具(こうぐ)- Tool', '種類(しゅるい)- Variety', '電気工事(でんきこうじ)- Electrical work'] | {電気}{工事}の{種類}と、その{工事}で{使用}する{工具}の{組合せ}として、{適切}なものは。 | バスダクト{工事} と ガストーチランプ | {合成}樹脂{管}{工事} と パイプベンダ | {金属}{線}ぴ{工事} と ボルトクリッパ | {金属}{管}{工事} と リーマ |  | 2018_2, 2017_2, 2016_1,
15 | What equipment is used in grid-connected solar cell power generation equipment? |  | Low voltage phase advance capacitor | Power conditioner | Dimmer | Automatic flasher | 2 | ['点滅器(てんめつき)- Flasher unit', '調光器(ちょうこうき)- Dimmer', '発電(はつでん)-Electricity generation', '太陽電池(たいようでんち)- Solar cell'] | 系統連系型の太陽{電池}{発電}{設備}において{使用}される{機器}は。 | {低圧}進相コンデンサ | パワーコンディショナ | {調光器} | {自動}{点滅器} |  | 2019_1, 2018_2, 2017_1,
16 | What is the name of the material shown in the photo? In addition, "Taishigaisen EM600V EEF / F1.6mm JIS JET <PS> E ◯◯ company Tainen 2017" is written on the surface of the material | Picture_16 | Inorganic insulation cable | 600V Vinyl Insulated Vinyl Sheath Cable Flat Type | 600V polyethylene insulated flame resistant polyethylene sheath cable flat type | 600V cross-linked polyethylene insulated vinyl sheath cable | 3 | ['耐燃性(たいねんせい)- Flame resistance', '絶縁(ぜつえん)-Breaking off relations', '無機(むき)- Inorganic', '表面(ひょうめん)- Surface', '材料(ざいりょう)- Materials', '写真(しゃしん)- Photograph'] | {写真}に{示す}{材料}の{名称}は。なお、{材料}の表面には「タイシガイセンEM600V EEF／F1.6mm JIS JET＜PS＞E◯◯社タイネン 2017」が記されている。 | 無機{絶縁}ケーブル | 600Vビニル{絶縁}ビニルシースケーブル平形 | 600Vポリエチレン{絶縁}{耐燃性}ポリエチレンシースケーブル平形 | 600V{架橋}ポリエチレン{絶縁}ビニルシースケーブル |  | 2018_2, 2015_2,
17 | What is the purpose of the equipment shown in the photo? | Picture_17 | Used as a selector switch for remote control relay operation. | It is used as an operation power transformer for remote control wiring. | Used as a relay for remote control wiring. | Used as a dimming switch for remote control. | 3 | ['変圧器(へんあつき)- Transformer', '電源(でんげん)- Electrical power', '操作(そうさ)- Operation', '配線(はいせん)- Wiring', '器具(きぐ)- Appliance'] | {写真}に{示す}{器具}の{用途}は。 {問題}{文}の{画像} | リモコン{リレー}{操作}用のセレクタ{スイッチ}として用いる。 | リモコン{配線}の{操作}{電源}{変圧器}として用いる。 | リモコン{配線}の{リレー}として用いる。 | リモコン用調光{スイッチ}として用いる。 |  | 2019_1, 2018_2,
18 | What are the uses of the tools shown in the photo? | Picture_18 | Used to remove the insulation coating of VFF cord (vinyl flat cord). | Used to strip off the exterior and insulation coating of CV cables (for low voltage). | Used to strip off the exterior and insulation of VVR cables. | Used to strip off the exterior and insulation of VVF cables. | 4 | ['絶縁(ぜつえん)- Breaking off relations', '被覆(ひふく)- Coating', '用途(ようと)- Use'] | {写真}に{示す}{工具}の{用途}は。 {問題}{文}の{画像} | VFFコード（ビニル平形コード）の{絶縁}{被覆}をはぎ取るのに用いる。 | CVケーブル（{低圧}用）の{外装}や{絶縁}{被覆}をはぎ取るのに用いる。 | VVRケーブルの{外装}や{絶縁}{被覆}をはぎ取るのに用いる。 | VVFケーブルの{外装}や{絶縁}{被覆}をはぎ取るのに用いる。 |  | 2019_2, 2018_2, 2016_2,
19 | What is the inappropriate connection between insulated wires in single-phase 100V indoor wiring work? |  | It was sufficiently covered with an insulated wire having an insulating effect equal to or higher than that of the insulated wire. | The electrical resistance of the wire has increased by 10%. | A ring sleeve (E type) was used to crimp the ends. | The tensile strength of the wire has been reduced by 15%. | 2 | ['終端部(しゅうたんぶ)- Trailer', '十分(じゅうぶん)- Enough', '相互(そうご)- Mutual', '効力(こうりょく)-Effect'] | {単相}100Vの{屋内配線}{工事}における{絶縁}{電線}{相互}の{接続}で、{不適切}なものは。 | {絶縁}{電線}の{絶縁}物と同等以上の{絶縁}{効力}のあるもので十分{被覆}した。 | {電線}の{電気}抵抗が10%{増加}した。 | {終端部}を{圧着}{接続}するのにリングスリーブ（E形）を{使用}した。 | {電線}の引張{強さ}が15%{減少}した。 |  | 2019_1, 2018_2, 2017_2,
20 | What is appropriate for low-voltage indoor wiring work that penetrates the metal plate (metal siding) wall of a wooden house? However, the electric wire used for metal pipe construction and metal flexible wire pipe construction shall be 600V vinyl insulated wire. |  | As for the cable work, the metal plate of the wall was sufficiently cut open, and the 600V vinyl insulated vinyl sheath cable was housed in a synthetic resin pipe to be electrically insulated and pierced. | As a metal pipe construction, a small-diameter hole was made in the wall, and the metal plate was brought into contact with the metal pipe to penetrate the metal pipe. | For the metal flexible conduit work, the metal plate of the wall was sufficiently cut open, and the metal flexible conduit was electrically connected to the wall and pierced. | The metal pipe work was carried out, and class D grounding work was performed on the metal pipe that was completely electrically connected to the metal plate of the wall, and the work was carried out through it. | 1 | ['貫通(かんつう)- Passing through', '壁(かべ)- Wall', '木造住宅(もくぞうじゅうたく)- Wooden house'] | {木造}{住宅}の{金属}板張り（{金属}系サイディング）の{壁}を貫通する{部分}の{低圧}{屋内配線}{工事}として、{適切}なものは。ただし、{金属}{管}{工事}、{金属}可とう{電線}{管}{工事}に{使用}する{電線}は、600Vビニル{絶縁}{電線}とする。 | ケーブル{工事}とし、{壁}の{金属}板張りを十分に切り開き、600Vビニル{絶縁}ビニルシースケーブルを{合成}樹脂{管}に収めて{電気}的に{絶縁}し、貫通{施工}した。 | {金属}{管}{工事}とし、{壁}に小径の穴を開け、{金属}板張りと{金属}{管}とを{接触}させ{金属}{管}を貫通{施工}した。 | {金属}可とう{電線}{管}{工事}とし、{壁}の{金属}板張りを十分に切り開き、{金属}製可とう{電線}{管}を{壁}と{電気}的に{接続}し、貫通{施工}した。 | {金属}{管}{工事}とし、{壁}の{金属}板張りと{電気}的に完全に{接続}された{金属}{管}にD{種}{接地}{工事}を施し、貫通{施工}した。 |  | 2018_2, 2016_2,
21 | What is the inappropriate construction method for single-phase three-wire 100 / 200V indoor wiring work in a wooden house? However, the wire used shall be a 600V vinyl insulated wire and a diameter of 1.6mm (annealed copper wire). |  | Two rigid vinyl chloride conduits (VE) of the same diameter were connected by TS coupling. | Flexible wire pipes (CD pipes) made of synthetic resin were piped under the wooden floor, inside the wall, and behind the ceiling. | Used in a concealed place where the metal pipe cannot be inspected. | The wire was passed through a synthetic resin flexible conduit (PF tube), and the distance between the support points was 1.0 m and fixed to the construction material. | 2 | ['穴(あな)- hole', '貫通(かんつう)- Passing through', '低圧(ていあつ)-Low pressure'] | {木造}{住宅}の{単相}３線式100／200V{屋内配線}{工事}で、{不適切}な{工事}{方法}は。ただし、{使用}する{電線}は600Vビニル{絶縁}{電線}、{直径}1.6mm（軟{銅線}）とする。 | {同じ}径の{硬質}塩化ビニル{電線}{管}（VE）２本をTSカップリングで{接続}した。 | {合成}樹脂製可とう{電線}{管}（CD{管}）を{木造}の{床}下や{壁}の{内部}及び{天井}裏に配{管}した。 | {金属}{管}を{点検}できない隠ぺい{場所}で{使用}した。 | {合成}樹脂製可とう{電線}{管}（PF{管}）内に通線し、支持点間の{距離}を1.0mで造営材に固定した。 |  | 2019_2, 2018_2, 2015_2,
22 | What is the inappropriate description of Class D grounding work to be applied to the metal outer box of wooden machinery and equipment? |  | An IV wire with a diameter of 1.6 mm was used for the ground wire of the outer box of the three-phase 200V motor. | A single core with a cross-sectional area of ​​0.75 mm 2 of a multi-core cord was used as the ground wire for a single-phase 100 V mobile electric drill (single insulation) . | A single-phase 100V motor was installed in a damp place, and a current-operated earth-leakage circuit breaker with a rated sensitivity current of 15mA and an operating time of 0.1 seconds was installed, so grounding work was omitted. | An electric round saw was connected to the secondary side electric circuit of the isolation transformer (secondary side ungrounded) of 200V on the primary side and 100V on the secondary side, and used without grounding. | 3 | ['場所(ばしょ)- Place', '単相(たんそう)- Single phase', '直径(ちょっけい)- Diamete', '外箱(そとばこ)- Outer case', '機械(きかい)- Machine', '木造(もくぞう)- Wooden'] | {機械}{器具}の{金属}製{外箱}に施すD{種}{接地}{工事}に関する{記述}で、{不適切}なものは。 | {三相}200V{電動機}{外箱}の{接地}線に{直径}1.6mmのIV{電線}を{使用}した。 | {単相}100V移動式の{電気}ドリル（一重{絶縁}）の{接地}{線}として多心コードの{断面積}0.75mm2の１心を{使用}した。 | {単相}100Vの{電動機}を{水気}のある{場所}に{設置}し、{定格}{感度}{電流}15mA、{動作時間}0.1秒の{電流}動作型{漏電}{遮断器}を取り付けたので、{接地}{工事}を{省略}した。 | 一次側200V、二次側100V、３kV・Aの{絶縁}{変圧器}（二次側非{接地}）の二次側{電路}に電動丸のこぎりを{接続}し、{接地}を施さないで{使用}した。 |  | 2018_2, 2017_1,
23 | When using a 600V vinyl insulated wire in a metal tube in low-voltage indoor wiring work, the current reduction coefficient for obtaining the allowable current of the wire is a combination of the number of wires in the same tube and the current reduction coefficient of the wire. What is wrong? However, the ambient temperature shall be 30 ° C or less. |  | 2 pieces 0.80 | 4 pieces 0.63 | 5 pieces 0.56 | 6 pieces 0.56 | 1 | ['ビニール (vinyl; plastic)', '周囲温度(しゅういおんど)- Ambient temperature', '係数(けいすう)- Coefficient', '電流(でんりゅう)- Electric current', '場合(ばあい)- Case'] | {低圧}{屋内配線}{工事}で、600Vビニル{絶縁}{電線}を{金属}管に収めて{使用}する{場合}、その{電線}の{許容}{電流}を求めるための{電流}{減少}{係数}{に関して}、同一{管内}の{電線}数と{電線}の{電流}{減少}{係数}との{組合せ}で、誤っているものは。ただし、{周囲}{温度}は30°C{以下}とする。 | 2 pieces 0.80 | 4 pieces 0.63 | 5 pieces 0.56 | 6 pieces 0.56 |  | 2018_2,
24 | What is wrong about the circuit resistance measurement of the analog circuit meter (built-in battery)? |  | Check that the battery capacity of the circuit meter is normal. | Switch to the resistance measurement range. If the approximate value of the object to be measured is assumed, the magnification of the measurement range should be appropriate. | Short the red and black measurement terminals (test leads) and adjust so that the pointer is 0 Ω. | Connect the red and black measurement terminals (test leads) to the object to be measured, and read the indicated value at that time. If the measurement range has a magnification display, the read indicated value is divided by the magnification to obtain the measured value. | 4 | ['電池(でんち)-Battery', '内蔵(ないぞう)- Internal ', '回路計(かいろけい)- Multimeter'] | アナログ式{回路}計（{電池}内蔵）の{回路}抵抗{測定}に関する{記述}として、誤っているものは。 | {回路}計の{電池}{容量}が正常であることを{確認}する。 | 抵抗{測定}レンジに切り換える。被{測定}{物の}概略{値}が想定される{場合}は、{測定}レンジの倍率を適正なものにする。 | 赤と黒の{測定}{端子}（テストリード）を短絡し、指針が０Ωになるよう調整する。 | 被{測定}物に、赤と黒の{測定}{端子}（テストリード）を{接続}し、その時の{指示}{値}を読む。なお、{測定}レンジに倍率{表示}がある{場合}は、読んだ{指示}{値}を倍率で割って{測定}{値}とする。 |  | 2018_2,
25 | It was a single-phase three-wire 100 / 200V indoor wiring, and three types of electric wires with insulation coating colors of red, white, and black were used. With this indoor wiring, the voltage between the wires and between the wires and the ground was measured. What is the appropriate combination of voltages as a result? However, the neutral line is white. |  | Red line and ground 200V, white line and ground 100V, black line and ground 0V | White line and black line 100V, red line and ground 0V, black line and ground 200V | Red line and White line between 200V, red line and ground 0V, black line and ground 100V | Red line and black line 200V, white line and ground 0V, red line and ground 100V | 4 | ['大(だい)- Large', '白色(しろいろ)-White', '赤色(あかいろ)- Red', '被覆(ひふく)-Coating', '単相(たんそう)- Single phase'] | {単相}３線式100／200V{屋内配線}で、{絶縁}{被覆}の色が{赤色}、白色、黒色の３{種類}の{電線}が{使用}されていた。この{屋内配線}で{電線}{相互}間及び{電線}と{大地}間の{電圧}を{測定}した。その{結果}としての{電圧}の{組合せ}で、{適切}なものは。ただし、中性線は白色とする。 | {赤色}{線}と{大地}間200V、白色{線}と{大地}間100V、黒色{線}と{大地}間 ０V | 白色{線}と黒色{線}間100V、{赤色}{線}と{大地}間０V、黒色{線}と{大地}間200V | {赤色}{線}と白色{線}間200V、{赤色}{線}と{大地}間０V、黒色{線}と{大地}間100V | {赤色}{線}と黒色{線}間200V、白色{線}と{大地}間０V、{赤色}{線}と{大地}間100V |  | 2018_2, 2015_1,
26 | When measuring the grounding resistance using a direct-reading grounding resistance meter, what is the most appropriate arrangement of the two auxiliary grounding poles P (for voltage) and C (for current) with respect to the grounding electrode E to be measured? |  | Picture_26_A | Picture_26_B | Picture_26_C | Picture_26_D | 3 | ['配置(はいち)- Arrangement', '抵抗(ていこう)- Resistance', '接地(せっち)- Ground (electricity)'] | 直読式{接地}抵抗計を用いて、{接地}抵抗を{測定}する{場合}、被{測定}{接地}{極}Eに対する、２つの{補助}{接地}{極}P（{電圧}用）及びC（{電流}用）の{配置}として、最も{適切}なものは。 | Picture_26_A | Picture_26_B | Picture_26_C | Picture_26_D |  | 2018_2, 2015_2,
27 | In the single-phase three-wire circuit as shown in the figure, when the switch was closed and the voltage across the device A was measured, it showed 120V. What are the possible causes for this? | Picture_27 | Line A is broken. | The neutral wire is broken. | Line B is broken. | The wire is broken inside device A. | 2 | ['内部(ないぶ)- Inside', '線(せん)-Line (e.g. telephone line); wire', '原因(げんいん)- Cause', '両端(りょうたん)- Both ends', '開閉器(かいへいき)- Switch'] | {図}のような{単相}３{線}式{回路}で、{開閉器}を閉じて{機器}Aの{両端}の{電圧}を{測定}したところ120Vを示した。この{原因}として、考えられるものは。 {問題}{文}の{画像} | a 線が{断線}している。 | 中性線が{断線}している。 | b 線が{断線}している。 | {機器}Aの{内部}で{断線}している |  | 2019_1, 2018_2,
28 | What is wrong with the description of the obligations or restrictions of the electrician? |  | An electrician must carry an electrician's diploma when engaging in electrical work as stipulated by the Electrician Law. . | When an electrician changes his / her name, he / she must apply to the prefectural governor who issued the diploma to have the diploma rewritten. | With a diploma only for a second-class electrician, you can engage in all the electrical work of the low-voltage part of a private electric facility whose maximum power of the demand equipment is less than 500 kW. | When an electrician performs electrical work specified by the Electrician Law, he / she must comply with the ministry ordinance that establishes technical standards for electrical equipment | 3 | ['記述(きじゅつ)-Description', '制限(せいげん)-Restriction', '義務(ぎむ)- Duty', '電気工事士(でんきこうじし)-Licensed electrician'] | {電気}{工事}士の{義務}又は{制限}に関する{記述}として、誤っているものは。 | {電気}{工事}士は、{電気}{工事}士法で定められた{電気}{工事}の{作業}に{従事}するときは、{電気}{工事}士{免状}を携帯していなければならない。 | {電気}{工事}士は、氏名を変更したときは、{免状}を交付した都{道}府県知事に申請して{免状}の書換えをしてもらわなければならない。 | 第二{種}{電気}{工事}士のみの{免状}で、{需要}{設備}の最大{電力}が500kW未満の自{家用}{電気}工{作物}の{低圧}{部分}の{電気}{工事}のすべての{作業}に{従事}することができる。 | {電気}{工事}士は、{電気}{工事}士法で定められた{電気}{工事}の{作業}を行うときは、{電気}{設備}に関する{技術基準}を定める{省令}に適合するよう{作業}を行わなければならない。 |  | 2018_2,
29 | What is applicable to specified electrical appliances under the Electrical Appliance and Material Safety Law? |  | Fluorescent lamp with power consumption of 40 W | Metal conduit with an outer diameter of 19 mm | Ventilation fan with power consumption of 30 W | Breaker for wiring with a rated current of 20 A | 4 | ['蛍光(けいこう)- Fluorescence', '用品(ようひん)- Articles', '特定(とくてい)- Specific', '電気用品安全法(でんきようひんあんぜんほう)- Electrical Appliance and Material Safety Act'] | {電気}{用品}安全法において、{特定}{電気}{用品}の{適用}を受けるものは。 | 消費{電力}40Wの蛍光ランプ | {外径}19mmの{金属}製{電線}{管} | 消費{電力}30Wの換気扇 | {定格}{電流}20Aの{配線}用{遮断器} |  | 2018_2, 2017_1, 2016_1,
30 | What is the correct combination of low voltage classifications in the "Ministry Ordinance that Establishes Technical Standards for Electrical Equipment"? |  | DC is 600V or less, AC is 600V or less | DC is 750V or less, AC is 600V or less | DC is 600V or less, AC 750V or less for direct current, | 750V or less for direct current, 750V or less for alternating current | 2 | ['以下(いか)- Not exceeding', '区分(くぶん)- Division', '省令(しょうれい)- Ministerial ordinance', '技術基準(ぎじゅつきじゅん)-Technical standards'] | 「{電気}{設備}に関する{技術基準}を定める{省令}」における{電圧}の{低圧}区分の{組合せ}で、{正しい}ものは。 | {直流}にあっては600V{以下}、{交流}にあっては600V{以下}のもの | {直流}にあっては750V{以下}、{交流}にあっては600V{以下}のもの | {直流}にあっては600V{以下}、{交流}にあっては750V{以下}のもの | {直流}にあっては750V{以下}、{交流}にあっては750V{以下}のもの |  | 2019_2, 2018_2, 2017_2,
31 | The part indicated by ① is a side note display of the automatic flasher. What is correct? |  | O | P | W | A | 4 | ['点滅器(てんめつき)-Switch (for a light)', '自動(じどう)-Automatic'] | ①で{示す}{部分}は{自動}{点滅器}の傍記{表示}である。{正しい}ものは。 | O | P | W | A |  | 2019_1, 2018_2,
32 | What is the name of the graphic symbol shown by②? |  | Remote control selector switch | Leakage alarm | Remote control transformer | Display switch | 1 | ['漏電(ろうでん)-Short circuit', '名称(めいしょう)- Name'] | ②で{示す}{図}{記号}の{名称}は。 | リモコンセレクタ{スイッチ} | {漏電}{警報器} | リモコン{トランス} | {表示}{スイッチ} |  | 2018_2, 2015_1,
33 | Where is the equipment with the graphic symbol shown in ③? |  | Floor surface | Ceiling surface | Wall surface 4. Double floor surface | Double floor surface | 2 | ['二重(にじゅう)- Double', '壁面(へきめん)- Surface of a wall', '床面(ゆかめん)- Floor'] | ③で{示す}{図}{記号}の{器具}の取り付け{場所}は。 | {床面} | {天井}面 | {壁面} | 二重{床面} |  | 2018_2, 2015_1,
34 | What is the pole arrangement (blade holder) of the outlet used for the part indicated by ④? |  | Picture_34_A | Picture_34_B | Picture_34_C | Picture_34_D | 4 | ['配置(はいち)- Arrangement ', '部分(ぶぶん)- Portion'] | ④で{示す}{部分}に{使用}する{コンセント}の{極}{配置}（刃受）は。 | Picture_34_A | Picture_34_B | Picture_34_C | Picture_34_D |  | 2018_2,
35 | What is (VE28) in the wiring of the part shown in ⑤? |  | A rigid vinyl chloride conduit with an outer diameter of 28 mm. | A flexible electric conduit made of synthetic resin with an outer diameter of 28 mm. | A rigid vinyl chloride conduit with an inner diameter of 28 mm. | Flexible conduit made of synthetic resin with an inner diameter of 28 mm. | 3 | ['内径(ないけい)- Bore', '配線(はいせん)- Wiring'] | ⑤で{示す}{部分}の{配線}で（VE28）とあるのは。 | {外径}28mmの{硬質}塩化ビニル{電線}{管}である。 | {外径}28mmの{合成}樹脂製可とう{電線}{管}である。 | {内径}28mmの{硬質}塩化ビニル{電線}{管}である。 | {内径}28mmの{合成}樹脂製可とう{電線}{管}である。 |  | 2018_2,
36 | What is the correct combination of the type of grounding work for the part indicated by ⑥ and the maximum allowable value [Ω] of the grounding resistance? No ground fault blocking device is installed on the power supply side of the drop line. |  | Class C grounding work 10Ω | Class C grounding work 50Ω | Class D grounding work 100Ω | Class D grounding work 500Ω | 3 | ['最大値(さいだいち)- Greatest value', '種類(しゅるい)- Variety'] | ⑥で{示す}{部分}の{接地}{工事}の{種類}及びその{接地}抵抗の{許容}される{最大値}［Ω］の{組合せ}として、{正しい}ものは。なお、引込{線}の{電源}側には地絡{遮断}装置は{設置}されていない。 | Class C grounding work 10Ω | Class C grounding work 50Ω | Class D grounding work 100Ω | Class D grounding work 500Ω |  | 2018_2,
37 | What is the graphic symbol of the equipment installed at the location indicated by ⑦? |  | Picture_37_A | Picture_37_B | Picture_37_C | Picture_37_D | 2 | ['図(ず)-Drawing', '箇所(かしょ)- Place'] | ⑦で{示す}{箇所}に{設置}する{機器}の{図}{記号}は。 | Picture_37_A | Picture_37_B | Picture_37_C | Picture_37_D |  | 2018_2,
38 | What is the minimum allowable value [MΩ] for the insulation resistance between the electric circuit and the ground in the part indicated by ⑧? |  | 0.1 | 0.2 | 0.4 | 1 | 1 | ['最小値(さいしょうち)- Minimum value', '電路(でんろ)- Electrical circuit'] | ⑧で{示す}{部分}の{電路}と{大地}間の{絶縁}抵抗として、{許容}される{最小}{値}［MΩ］は。 | 0.1 | 0.2 | 0.4 | 1 |  | 2018_2,
39 | What is the purpose of using the equipment with the graphic symbols shown in ⑨? |  | Cut off the overcurrent. | Cut off the ground fault current. | Cut off overcurrent and ground fault current. | Cut off the unbalanced current. | 1 | ['不平衡(ふへいこう)- Imbalance', '目的(もくてき)- Purpose', '器具(きぐ)- Instrument'] | ⑨で{示す}{図}{記号}の{器具}を用いる{目的}は。 | 過{電流}を{遮断}する。 | 地絡{電流}を{遮断}する。 | 過{電流}と地絡{電流}を{遮断}する。 | {不平衡}{電流}を{遮断}する。 |  | 2018_2,
40 | What is the minimum number of wires (core wire number) in part ⑩? |  | 2 | 3 | 4 | 5 | 2 | ['本数(ほんすう)- Number', '部分(ぶぶん)- Portion'] | ⑩の{部分}の{最少}{電線}{本数}（心線数）は。 | 2 | 3 | 4 | 5 |  | 2018_2,
41 | What is the correct combination of ring sleeve type, number and engraving when pressure bonding the connection work of the part shown in ⑪ with ring sleep? However, the ◯, small, and middle in the center of the ring sleeve shown in the photo indicate the engraving. |  | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D | 1 | ['種類(しゅるい)- Variety; kind', '場合(ばあい)- Case', '圧着(あっちゃく)-Pressure bonding', '接続(せつぞく)- Connection'] | ⑪で{示す}{部分}の{接続}{工事}をリングスリープで{圧着}{接続}する{場合}のリングスリーブの{種類}、{個数}及び{刻印}の{組合せ}で、{正しい}ものは。ただし、{写真}に{示す}リングスリーブ{中央}の◯、小、中は{刻印}を表す。 | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D |  | 2018_2,
42 | What is used to connect the conduits shown in ⑫? |  | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D | 3 | ['使用(しよう)-Use', '相互(そうご)- Mutual'] | ⑫で{示す}{電線}{管}{相互}を{接続}するために{使用}されるものは。 | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D |  | 2018_2, 2018_1, 2017_2,
43 | Tools that are not commonly used in wiring work for the parts shown in ⑬. |  | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D | 1 | ['一般的(いっぱんてき)- Common', 'はいせんこうじ', '配線工事'] | ⑬で{示す}{部分}の{配線}{工事}で{一般的}に{使用}されることのない{工具}は。 | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D |  | 2018_2,
44 | What can measure the leakage current of the circuit shown in ⑭? |  | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D | 1 | ['測定(-そくてい)- Measurement', '回路(かいろ)- Circuit'] | ⑭で{示す}{回路}の漏れ{電流}を{測定}できるものは。 | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D |  | 2018_2,
45 | The equipment used for the graphic symbol shown in ⑮ |  | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D | 4 | ['記号(きごう)- Symbol'] | ⑮で{示す}{図}{記号}の{部分}に{使用}される{機器}は。 | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D |  | 2018_2,
46 | What is the tool for crimping the crimp terminal and ground wire shown in the photo in part ⑯? | Picture_46 | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D | 4 | ['圧着端子(あっちゃくたんし)- Crimp contact', '写真(しゃしん)- Photograph'] | ⑯の{部分}で{写真}に{示す}{圧着}{端子}と{接地}{線}を{圧着}{接続}するための{工具}は。 | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D |  | 2018_2, 2017_1,
47 | What is the instrument with the graphic symbol shown in ⑰? However, the figure below the photograph shows the configuration of the contacts. |  | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D | 4 | ['接点(せってん)- Tangent point', '器具(きぐ)- Instrument'] | ⑰で{示す}{図}{記号}の{器具}は。ただし、{写真}下の{図}は、{接点}の{構成}を{示す}。 | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D |  | 2019_1, 2018_2,
48 | If all the connections in the VVF joint box shown in ⑱ are crimp connections, what is the correct combination of the type of ring sleeve to be used and the minimum number? However, ground wiring shall also be included. |  | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D | 2 | ['種類(しゅるい)- Type', '場合(ばあい)- Case'] | ⑱で{示す}VVF用ジョイントボックス内の{接続}をすべて{圧着}{接続}とする{場合}、{使用}するリングスリーブの{種類}と{最少}{個数}の{組合せ}で、{正しい}ものは。ただし、{接地}{配線}も含まれるものとする。 | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D |  | 2018_2,
49 | If all the connections in the VVF joint box shown in ⑲ are plug-in connectors, what is the correct combination of the type of plug-in connector to be used and the minimum number of connectors? However, all wires used shall be VVF1.6. |  | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D | 2 | ['最少(さいしょう)- Fewest', '接続(せつぞく)- Connection'] | ⑲で{示す}VVF用ジョイントボックス内の{接続}をすべて差込形{コネクタ}とする{場合}、{使用}する差込形{コネクタ}の{種類}と{最少}{個数}の{組合せ}で、{正しい}ものは。ただし、{使用}する{電線}はすべてVVF1.6とする。 | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D |  | 2018_2,
50 | In this wiring diagram, what are the unused outlets? |  | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D | 4 | ['配線図(はいせんず)- Wiring diagram'] | この{配線}{図}で、{使用}されていない{コンセント}は。 | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D |  | 2018_2,