## Sheet1
no | Eng | Picture | Option_1_Eng | Option_2_Eng | Option_3_Eng | Option_4_Eng | Ans | Vocab | Jpn | Option_1_Jpn | Option_2_Jpn | Option_3_Jpn | Option_4_Jpn | Exp | comment
1 | In the circuit shown in the figure, when the switch S is closed, the voltage [V] between the a and b terminals is. | Picture_1 | 3 | 4 | 50 | 60 | 4 | ['電圧(でんあつ)- Voltage', '回路(かいろ)- Circuit'] | {図}のような{回路}で、{スイッチ}Sを閉じたとき、a -b {端子}間 の{電圧} ［V］は。 | 3 | 4 | 50 | 60 | Voltage = 120V R = 50Ω + 50Ω = 100Ω (120V/100Ω) A = 1.2A 50Ω x 1.2A = 60V | 2019_1, 2015_2,
2 | When the diameter of the conductor of a vinyl insulated wire (single core) is D and the length is L, what is wrong as a description about the resistance and allowable current of this wire? |  | The permissible current increases as the ambient temperature rises. | The resistance of the wire is inversely proportional to D ^ 2. | The resistance of the wire is proportional to L. | The allowable current increases as D increases. | 1 | ['電流(でんりゅう) -Electric current', '許容(きょよう)- Permission', '導体(どうたい)- Conductor (electricity)', '電線(でんせん)- Cable'] | ビニル{絶縁}{電線}（単心）の{導体}の{直径}をD、{長さ}をLとするとき、この{電線}の抵抗と{許容}{電流}に関する{記述}として、誤っているものは。 | {許容}{電流}は、{周囲}の{温度}が上昇すると、大きくなる。 | {電線}の抵抗は、D2に反比例する。 | {電線}の抵抗は、Lに比例する。 | {許容}{電流}は、Dが大きくなると、大きくなる |  | 2019_1, 2018_1, 2016_1,
3 | What is the amount of electric power [kW ・ h] required to raise the temperature of 60 kg of water by 20 K using an electric heater? However, the specific heat of water is 4.2 kj / (kg · K) and the thermal efficiency is 100%. |  | 1 | 1.2 | 1.4 | 1.6 | 3 | ['熱効率(ねつこうりつ)- Thermal efficiency', '比熱(ひねつ)- Specific heat', '電力量(でんりょくりょう)- Electric potential energy', '温度(おんど)- Temperature'] | {電熱器}により、60kgの水の{温度}を20K上昇させるのに{必要}な{電力}量［kW・h］は。 ただし、水の{比熱}は4.2kJ／（kg・K）とし、{熱効率}は100%とする | 1 | 1.2 | 1.4 | 1.6 | Heat = 4.2kJ/(kg K) x 60kg x 20K = 5040kJ 1 kW・h = 3600 kJ to convert to the unit of electric energy. 5040kJ/3600kJ = 1.4kW・h | 2019_1, 2018_2, 2015_2,
4 | In the AC circuit as shown in the figure, the voltage V [V] across the resistance 8Ω is. | Picture_4 | 43 | 57 | 6 | 8 | 4 | ['両端(りょうたん)- Both ends', '交流(こうりゅう)- Alternating current'] | {図}のような{交流}{回路}において、抵抗８Ωの{両端}の{電圧}V［V］は。 | 43 | 57 | 6 | 8 | Impedance = √R^2 + XL^2 = √8^2 + 6^2 = √64+36 = √100 = 10 [Ω] So, I = V/R = 100/10 = 10 [A] V = IR = 10 x 8 = 80 [V] | 2019_1, 2018_2, 2017_2, 2016_1,
5 | What is the total power consumption [kW] of the three-phase three-wire circuit as shown in the figure? | Picture_5 | 2.4 | 4.8 | 9.6 | 19.2 | 3 | ['抵抗(ていこう)- Resistance', '交流(こうりゅう)- Alternating current'] | {図}のような{三相}３{線}式{回路}の全消費{電力}［kW］は。 | 2.4 | 4.8 | 9.6 | 19.2 | Impedance = √R^2 + XL^2 = √8^2 + 6^2 = √64+36 = √100 = 10 [Ω] I = 200 ÷ 10 = 20 [A] Power factor = 8 / 10 = 0.8 Power consumption = 200 Vx 20A x 0.8 = 3200 [W] Since there are three phases, 3200 x 3 = 9600 [W] = 9.6 [kW] | 2019_1, 2017_2,
6 | In a single-phase two-wire circuit as shown in the figure, when the voltage between c and c'is 100V, the voltage [V] between a and a'is. However, r is the electrical resistance [Ω] of the electric wire. | Picture_6 | 102 | 103 | 104 | 105 | 4 | ['電気抵抗(でんきていこう)- Electrical resistance and conductance', '回路(かいろ)- Circuit', '単相(たんそう)- Single phase'] | {図}のような{単相}２線式{回路}において、c - c’ 間の{電圧}が100Vのとき、a - a’ 間の{電圧}［V］は。 ただし、rは{電線}の{電気}抵抗［Ω］とする。 | 102 | 103 | 104 | 105 | V = IR = 10 x 0.1 = 1 [V] V = IR = 15 x 0.1 = 1.5 [V] Voltage between aa = 100 + 1 + 1 + 1.5 + 1 .5 = 105 [V] | 2019_1, 2015_2,
7 | In a single-phase three-wire circuit as shown in the figure, when the resistance per wire is r [Ω], the load current is I [A], and the current flowing through the neutral wire is 0A, the voltage drop (Vs --Vr). The formula for [V] is. | Picture_7 | 2rl | 3rl | rl | √3rl | 3 | ['電圧降下(でんあつこうか) -Voltage drop', '電流(でんりゅう)- Electric current', '当たり(あ)- Hit'] | {図}のような{単相}３線式{回路}で、{電線}１線{当たり}の抵抗がr［Ω］、{負荷}{電流}がI［A］、中性線に{流れる}{電流}が０Aのとき、{電圧}降下（Vs - Vr）［V］を{示す}式は。 | 2rl | 3rl | rl | √3rl | e＝Vs-Vr ＝(rI＋Vr)-Vr ＝rI | 2019_1,
8 | When installing five 600V vinyl insulated wires (annealed copper wires) with a diameter of 2.0 mm in a low-pressure indoor wiring work using a metal pipe, the permissible current [A] per wire is. However, the ambient temperature shall be 30 ° C or less, and the current reduction coefficient shall be 0.56. |  | 10 | 15 | 19 | 27 | 3 | ['係数(けいすう)- Coefficient', '周囲温度(しゅういおんど)- Ambient temperature', '減少(げんしょう)- Decrease', '銅線(どうせん)- Copper line', '管内(かんない)- In a pipe'] | {金属}管による{低圧}{屋内配線}{工事}で、{管内}に{直径}2.0mmの600Vビニル{絶縁}{電線}（軟{銅線}）５本を収めて{施設}した{場合}、{電線}１本{当たり}の{許容}{電流}［A］は。 ただし、{周囲}{温度}は30°C{以下}、{電流}{減少}{係数}は0.56とする。 | 10 | 15 | 19 | 27 | 35×0.56＝19.6 [A] | 2019_1, 2018_1, 2017_1, 2016_2, 2015_2,
9 | When branching from a low-voltage indoor trunk line protected by an overcurrent circuit breaker with a rated current of 100 A as shown in the figure and installing an overcurrent circuit breaker at a position of 6 m, the minimum allowable current of the wire between a and b [ A] is | Picture_9 | 25 | 35 | 45 | 55 | 2 | ['最小値(さいしょうち)- Minimum value', '遮断器(しゃだんき)- Circuit breaker', '過電流(かでんりゅう)- Excess current', '定格(ていかく)- Rated value'] | {図}のように{定格}{電流}100Aの過{電流}{遮断器}で保護された{低圧}{屋内}{幹線}から{分岐}して、６mの{位置}に過{電流}{遮断器}を{施設}するとき、a - b間の{電線}の{許容}{電流}の{最小}{値}［A］は、 | 25 | 35 | 45 | 55 | the rated current of the main line is 100 [A], so it is obtained by the following formula. 100×0.35＝35 [A] | 2019_2, 2019_1, 2018_1, 2018_2, 2016_2, 2016_1, 2015_1, 2015_2,
10 | What is the inappropriate combination of the rated current of the molded case circuit breaker and the outlet in the design of the branch circuit of the low voltage indoor wiring? |  | 2 outlets with rated current of 30A | 2 outlets with rated current of 15A | 1 outlet with rated current of 20A | 2 outlets with rated current of 15A | 2 | ['定格(ていかく)- Rated value', '設計(せっけい)- plan; design', '分岐(ぶんき)- Divergence', '屋内配線(おくないはいせん)- Interior wiring'] | {低圧}{屋内配線}の{分岐}{回路}の{設計}で、配線用{遮断器}の{定格}{電流}と{コンセント}の{組合せ}として、{不適切}なものは。 | Figure_10_A#{定格}{電流} 30Aの {コンセント}2個 | Figure_10_B#{定格}{電流} 15Aの {コンセント}2個 | Figure_10_C#{定格}{電流} 20Aの {コンセント}1個 | Figure_10_D#{定格}{電流} 15Aの {コンセント}2個 |  | 2019_1, 2018_1, 2017_1,
11 | What is the inappropriate way to use the outlet box (made of metal)? |  | Used to facilitate the pulling in of electric wires in metal pipe construction. | Used for the part that connects electric wires to each other in metal pipe construction. | Used to collect and install molded case circuit breakers. | Used when pulling out an electric wire at the part where lighting equipment is attached. | 3 | ['相互(そうご)-mutual', '使用方法(しようほうほう)- How to use', '金属製(きんぞくせい)-Made of metal'] | アウトレットボックス（{金属}製）の{使用}{方法}として、{不適切}なものは。 | {金属}{管}{工事}で{電線}の引き入れを{容易}にするのに用いる。 | {金属}{管}{工事}で{電線}{相互}を{接続}する{部分}に用いる。 | {配線}用{遮断器}を{集合}して{設置}するのに用いる。 | 照明{器具}などを取り付ける{部分}で{電線}を引き出す{場合}に用いる。 |  | 2019_1, 2017_2, 2016_1,
12 | Equipment installed indoors with a working voltage of 300V or less that can use a vinyl cord for the attached moving wire. |  | Electric fan | Electric kotatsu | Electric stove | Electric toaster | 1 | ['電気こんろ(でんき)- Electric cooking stove. ', '炬燵(こたつ)- Kotatsu; table over an electric heater with a hanging quilt that retains heat.', '屋内(おくない) -Indoor', '電圧(でんあつ)- Voltage'] | {使用}{電圧}が300V{以下}の{屋内}に{施設}する{器具}であって、付属する移動{電線}にビニルコードが{使用}できるものは。 | {電気}扇風機 | {電気}こたつ | {電気}こんろ | {電気} トースター |  | 2019_1, 2016_2,
13 | What is the appropriate combination of tools used for cutting and bending work in metal conduit (steel conduit) construction? |  | File, pipe wrench, torch lamp | Reamer, gold cutting saw, pipe bender | File, gold saw, torch lamp | Reamer, pipe wrench, pipe bender | 2 |  | {金属}{管}（{鋼製}{電線}{管}）{工事}で{切断}及び曲げ{作業}に{使用}する{工具}の{組合せ}として、{適切}なものは。 | やすり、パイプレンチ、トーチランプ | リーマ、金切りのこ、パイプベンダ | やすり、金切りのこ、トーチランプ | リーマ、パイプレンチ、パイプベンダ |  | 2019_1, 2018_1, 2016_2, 2015_1,
14 | When using a three-phase squirrel-cage induction motor with 6 poles at a frequency of 50 Hz, the closest rotation speed [min-1] is |  | 500 | 1000 | 1500 | 3000 | 4 | ['速度(そくど)- Velocity', '回転(かいてん)- Rotation', '周波数(しゅうはすう)- Frequency'] | {極}数６の{三相}かご形{誘導電動機}を{周波数}50Hzで{使用}するとき、最も近い{回転}{速度}［min-1］は。 | 500 | 1000 | 1500 | 3000 |  | 2019_1, 2018_2, 2018_1, 2015_2,
15 | What kind of equipment is used in grid-connected small-power photovoltaic power generation equipment? |  | Dimmer | Low-voltage phase-advancing capacitor | Automatic flasher | Power conditioner | 4 | ['調光器(ちょうこうき)- Dimmer', '機器(きき)- Equipment'] | 系統連系型の小{出力}太陽光{発電}{設備}において、{使用}される{機器}は。 | {調光器} | {低圧}進相コンデンサ | {自動}{点滅器} | パワーコンディショナ |  | 2019_1, 2018_2, 2017_1,
16 | What are the uses of the materials shown in the photo? | Picture_16 | Used to install switches and outlets in a house. | Used in places where many metal pipes gather. | Used at intersections of floor ducts. | Used to collectively install a large number of circuit breakers. | 1 | ['箇所(かしょ)- Place', '多数(たすう)- Large number ', '住宅(じゅうたく)- Residence; Housing'] | {写真}に{示す}{材料}の{用途}は。 | {住宅}で{スイッチ}や{コンセント}を取り付けるのに用いる。 | {多数}の{金属}{管}が{集合}する{箇所}に用いる。 | フロアダクトが交差する{箇所}に用いる。 | {多数}の{遮断器}を{集合}して{設置}するために用いる。 |  | 2019_1, 2016_2,
17 | What is the purpose of the equipment shown in the photo? | Picture_17 | Use as an operation power transformer for remote control wiring | Used as a relay for remote control wiring | Used as a selector switch for remote control relay operation. | Used as a dimming switch for remote control. | 2 | ['操作(そうさ)- Operation; Management', '画像(がぞう)- Image; Picture', '用途(ようと)- Use; Service'] | {写真}に{示す}{器具}の{用途}は。 | リモコン{配線}の{操作}{電源}{変圧器}として用いる。 | リモコン{配線}の{リレー}として用いる。 | リモコン{リレー}{操作}用のセレクタ{スイッチ}として用いる。 | リモコン用調光{スイッチ}として用いる。 |  | 2019_1, 2018_2,
18 | What are the uses of the tools shown in the photo? | Picture_18 | Used for bending rigid vinyl chloride conduit. | Used for connecting flexible conduits made of synthetic resin. | Used for bending lighting ducts. | Used for bending metal pipes (copper conduits). | 1 | ['銅製(どうせい)- Made of copper', '接続(せつぞく)- Connection', '硬質(こうしつ)- Hardness'] | {写真}に{示す}{工具}の{用途}は。 | {硬質}塩化ビニル{電線}{管}の曲げ加工に用いる。 | {合成}樹脂製可とう{電線}{管}の{接続}加工に用いる。 | ライティングダクトの曲げ加工に用いる。 | {金属}{管}（{銅製}{電線}{管}）の曲げ加工に用いる。 |  | 2019_1, 2016_1,
19 | What is the inappropriate connection between insulated wires in single-phase 100V indoor wiring work? |  | Sufficiently covered with an insulated wire with an insulating effect equal to or higher than that of the insulated wire. | The tensile strength of the wire has decreased by 15%. | The wires were twisted strongly with fingers, and the part was sufficiently covered with insulating tape. | Connected so that the electrical resistance of the connection does not increase. | 3 | ['効力(こうりょく)- Effect', '強さ(つよ)- Strength; power'] | {単相}100Vの{屋内配線}{工事}における{絶縁}{電線}{相互}の{接続}で、{不適切}なものは。 | {絶縁}{電線}の{絶縁}物と同等以上の{絶縁}{効力}のあるもので十分{被覆}した。 | {電線}の引張{強さ}が15%{減少}した。 | {電線}{相互}を指で強くねじり、その{部分}を{絶縁}テープで十分{被覆}した。 | {接続}部の{電気}抵抗が{増加}しないように{接続}した。 |  | 2019_1, 2018_2, 2017_2,
20 | What is inappropriate for 100V low voltage indoor wiring work? |  | In the floor duct work, the length of the duct is short, so the D-class grounding work was omittaced | During the cable construction, the facility was installed so that the vinyl exterior cable and the weak current electric wire would not come into contact with each other. | In the metal pipe construction, the wire lath of the penetrating part of the wire lath was sufficiently cut open, and the metal pipe of the penetrating part was housed in the synthetic resin pipe. | In the synthetic resin pipe construction, the distance between the support points of the pipe was set to 1.5 m. | 1 | ['距離(きょり)- Distance', '箇所(かしょ)- Place', '外装(がいそう)- Exterior', '長さ(なが)- Length', '低圧(ていあつ)- Low voltage'] | 100Vの{低圧}{屋内配線}{工事}で、{不適切}なものは。 | フロアダクト{工事}で、ダクトの{長さ}が短いのでD{種}{接地}{工事}を{省略}した。 | ケーブル{工事}で、ビニル{外装}ケーブルと弱{電流}{電線}が{接触}しないように{施設}した。 | {金属}{管}{工事}で、ワイヤラス張りの貫通{箇所}のワイヤラスを十分に切り開き、貫通{部分}の{金属}{管}を{合成}樹脂{管}に収めた。 | {合成}樹脂{管}{工事}で、その{管}の支持点間の{距離}を1.5mとした。 |  | 2019_1,
21 | A three-phase three-wire 200V room air conditioner with a rated power consumption of 2.5kW was installed indoors in a house with a store. What is the appropriate construction method for the electric circuit that supplies electricity to this room air conditioner? However, contact protection measures shall be taken for the wiring, and parts that may be touched by people such as the outer box of the room air conditioner shall be made of a rigid material with insulating material. |  | We installed a dedicated overcurrent circuit breaker, wired it with synthetic resin pipe work, and connected it to the room air conditioner using an outlet. | A dedicated earth-leakage circuit breaker (with overload protection) was installed, wired by cable construction, and directly connected to the room air conditioner. | We installed a dedicated molded case circuit breaker, wired it with metal pipe work, and connected it to the room air conditioner using an outlet. | Only a dedicated switch was installed, wiring was done by metal pipe construction, and it was directly connected to the room air conditioner. | 2 | ['開閉器(かいへいき)- Switch', '専用(せんよう)- Private use; Personal use', '防護(ぼうご)- Protection', '方法(ほうほう)- Method; process', '定格(ていかく)- Rated value'] | {店舗}付き{住宅}の{屋内}に{三相}３線式200V、{定格}消費{電力}2.5kWのルームエアコンを{施設}した。このルームエアコンに{電気}を供給する{電路}の{工事}{方法}として、{適切}なものは。 ただし、{配線}は{接触}{防護}{措置}を施し、ルームエアコン{外箱}等の人が触れるおそれがある{部分}は{絶縁}性のある{材料}で堅ろうに作られているものとする。 | {専用}の過{電流}{遮断器}を{施設}し、{合成}樹脂{管}{工事}で{配線}し、{コンセント}を{使用}してルームエアコンと{接続}した。 | {専用}の{漏電}{遮断器}（{過負荷}保護付）を{施設}し、ケーブル{工事}で{配線}し、ルームエアコンと{直接}{接続}した。 | {専用}の{配線}用{遮断器}を{施設}し、{金属}{管}{工事}で{配線}し、{コンセント}を{使用}してルームエアコンと{接続}した。 | {専用}の{開閉器}のみを{施設}し、{金属}{管}{工事}で{配線}し、ルームエアコンと{直接}{接続}した。 |  | 2019_1,
22 | When performing grounding work on the iron base of a three-phase induction motor with a rated voltage of 200V and a rated output of 2.2kW fixed on the floor, what is the inappropriate combination of the thickness of the grounding wire (annealed copper wire) and the grounding resistance value? However, an earth-leakage circuit breaker shall not be installed. |  | Diameter 1.6mm, 10Ω | Diameter 2.0mm, 50Ω | Nominal cross-sectional area 0.75mm2, 5Ω | Diameter 2.6mm, 75Ω | 3 | ['場合(ばあい)- Case; Situation', '出力(しゅつりょく)- Output', '床(ゆか)- Floor'] | {床}に固定した{定格}{電圧}200V、{定格}{出力}2.2kWの{三相}{誘導電動機}の鉄台に{接地}{工事}をする{場合}、{接地}線（軟{銅線}）の太さと{接地}抵抗{値}の{組合せ}で、{不適切}なものは。ただし、{漏電}{遮断器}を{設置}しないものとする。 | {直径}1.6mm、10Ω | {直径}2.0mm、50Ω | {公称}{断面積}0.75mm2、5Ω | {直径}2.6mm、75Ω |  | 2019_1, 2016_1,
23 | What is inappropriate for use at the end A or B of metal pipe construction installed outside the rain line shown in the figure? |  | An entrance cap was used for the A part. | A terminal cap was used for the B part. | An entrance cap was used for the B part. | A terminal cap was used for the A part. | 4 | ['部分(ぶぶん)- Portion', '文(ぶん)- Sentence', '末端(まったん)- End'] | {図}に{示す}雨{線}外に{施設}する{金属}{管}{工事}の{末端}A又はB{部分}に{使用}するものとして、{不適切}なものは。 {問題}{文}の{画像} | A{部分}にエン{トランス}キャップを{使用}した。 | B{部分}にターミナルキャップを{使用}した。 | B{部分}にエン{トランス}キャップを{使用}した。 | A{部分}にターミナルキャップを{使用}した。 |  | 2019_1,
24 | In the single-phase three-wire circuit as shown in the figure, when the switch was closed and the voltage across the device A was measured, it showed 150V. What are the possible causes for this? |  | The wire is broken inside device A. | The a line is broken. | The b line is broken. | The neutral wire is broken. | 4 | ['内部(ないぶ)- Interior', '両端(りょうたん)- Both ends', '原因(げんいん)- Cause'] | {図}のような{単相}３{線}式{回路}で、{開閉器}を閉じて{機器}Aの{両端}の{電圧}を{測定}したところ150Vを示した。この{原因}として、考えられるものは。 {問題}{文}の{画像} | {機器}Aの{内部}で{断線}している。 | a線が{断線}している。 | b線が{断線}している。 | 中性線が{断線}している。 |  | 2019_1, 2018_2,
25 | Since it was difficult to measure the insulation resistance in an electric circuit with a low working voltage, the insulation performance was confirmed by the leakage current when the working voltage was applied. The maximum value [mA] of the leakage current that can be judged to have insulation performance, as defined in "Interpretation of Technical Standards for Electrical Equipment", is |  | 0.1 | 0.2 | 1 | 2 | 3 | ['解釈(かいしゃく)- Interpretation', '性能(せいのう)- Ability', '漏洩(ろうえい)- Leak', '状態(じょうたい)- State', '測定(そくてい)- Measurement'] | {使用}{電圧}が{低圧}の{電路}において、{絶縁}抵抗{測定}が困難であったため、{使用}{電圧}が加わった{状態}で漏えい{電流}により{絶縁}{性能}を{確認}した。「{電気}{設備}の{技術基準}の{解釈}」に定める、{絶縁}{性能}を有していると{判断}できる漏えい{電流}の{最大値}［mA］は、 | 0.1 | 0.2 | 1 | 2 |  | 2019_1, 2017_1,
26 | The insulation resistance value [MΩ] of the wiring to the 200V three-phase induction normal motion machine (ground voltage 200V) of the factory and the grounding resistance value [Ω] of the iron base of this motor were measured. What is the appropriate combination of measured values ​​that meets the technical standards for electrical equipment? However, the operating time of the earth-leakage circuit breaker installed in the 200V electric circuit shall be 0.1 seconds. |  | 0.2MΩ、300Ω | 0.4MΩ、600Ω | 0.1MΩ、200Ω | 0.1MΩ、50Ω | 1 | ['配線(はいせん)- Wiring', '測定値(そくていち)- Measured value', '誘導(ゆうどう)- Guidance', '工場(こうじょう)- Factory'] | {工場}の200V{三相}{誘導}正動機（{対地}{電圧}200V）への{配線}の{絶縁}抵抗{値}［MΩ］及びこの{電動機}の鉄台の{接地}抵抗{値}［Ω］を{測定}した。{電気}{設備}{技術基準}等に適合する{測定}{値}の{組合せ}として、{適切}なものは。 ただし、200V{電路}に{施設}された{漏電}{遮断器}の{動作時間}は0.1秒とする。 | 0.2MΩ、300Ω | 0.4MΩ、600Ω | 0.1MΩ、200Ω | 0.1MΩ、50Ω |  | 2019_1,
27 | What is the correct measurement method when measuring the presence or absence of leakage current in a single-phase three-wire circuit using a clamp-type leakage ammeter? However, the following line indicates the neutral line. |  | Picture_27_A | Picture_27_B | Picture_27_C | Picture_27_D | 4 | ['測定方法(そくていほうほう)- Measuring method', '漏れ電流(もでんりゅう)- Leakage current'] | {単相}３{線}式{回路}の漏れ{電流}の有無を、クランプ形漏れ{電流}計を用いて{測定}する{場合}の{測定}{方法}として、{正しい}ものは。 ただし、{以下}{線}は中性{線}を{示す}。 | Picture_27_A | Picture_27_B | Picture_27_C | Picture_27_D |  | 2019_1, 2017_2, 2015_1,
28 | What is wrong with the description of the obligations or restrictions of the electrician? |  | An electrician must report when requested by the prefectural governor to report on the work of electrical work. | An electrician must carry an electrician's diploma when engaging in the work of electrical work stipulated by the Electrician Law. | When an electrician engages in electrical work specified by the Electrician Law, he / she must comply with the "Ministry Ordinance that Establishes Technical Standards for Electrical Equipment". | When an electrician changes his / her address, he / she must apply to the prefectural governor who issued the diploma to have the diploma rewritten. | 4 | ['電気工事士(でんきこうじし)-Electrician ', '業務(ぎょうむ)- Business', '記述(きじゅつ)- Description', '制限(せいげん)- Restriction', '義務(ぎむ)- Duty'] | {電気}{工事}士の{義務}又は{制限}に関する{記述}として、誤っているものは。 | {電気}{工事}士は、都{道}府県知事から{電気}{工事}の{業務}{に関して}報告するよう求められた{場合}には、報告しなければならない。 | {電気}{工事}士は、{電気}{工事}士法で定められた{電気}{工事}の{作業}に{従事}するときは、{電気}{工事}士{免状}を携帯しなければならない。 | {電気}{工事}士は、{電気}{工事}士法で定められた{電気}{工事}の{作業}に{従事}するときは、「{電気}{設備}に関する{技術基準}を定める{省令}」に適合するよう{作業}を行わなければならない。 | {電気}{工事}士は、{住所}を変更したときは、{免状}を交付した都{道}府県知事に申請して{免状}の書換えをしてもらわなければならない。 |  | 2019_1,
29 | What is wrong with the description of electrical appliances in the Electrical Appliance and Material Safety Law? |  | A person who manufactures or imports electrical appliances may attach a label according to the method specified by the Ordinance of the Ministry of Economy, Trade and Industry when he / she fulfills the obligations stipulated in the Electrical Appliance and Material Safety Law. | Specified electrical appliances are labeled with (PSE) or (PS) E. | A person who sells electrical appliances shall not sell electrical appliances that are not labeled by law, except with the approval of the Minister of Economy, Trade and Industry. | An electrician shall not use electrical equipment that is not labeled as stipulated in the Electrical Appliance and Material Safety Law for the installation or modification of electric facilities. | 2 | ['表示(ひょうじ)- Indication', '販売(はんばい)-Sales', '方式(ほうしき)- Form; Method', '事業(じぎょう)- Project', '輸入(ゆにゅう)- Import', '製造(せいぞう)- Manufacture', '用品(ようひん)- Equipment'] | {電気}{用品}安全法における{電気}{用品}に関する{記述}として、誤っているものは。 | {電気}{用品}の{製造}又は{輸入}の{事業}を行う者は、{電気}{用品}安全法に規定する{義務}を履行したときに、経済産業{省令}で定める{方式}による{表示}を付すことができる。 | {特定}{電気}{用品}には(PS)Eの{表示}が付されている。 | {電気}{用品}の{販売}の{事業}を行う者は、経済産業大臣の承認を受けた{場合}等を除き、{法令}に定める{表示}のない{電気}{用品}を{販売}してはならない。 | {電気}{工事}士は、{電気}{用品}安全法に規定する{表示}の付されていない{電気}{用品}を{電気}工{作物}の{設置}又は変更の{工事}に{使用}してはならない |  | 2019_2, 2019_1, 2018_1,
30 | What is wrong with the description of electric facilities for general use? |  | Those that receive power at low voltage and have a solar cell power generation facility with an output of 60 kW on the same premises are electric facilities for general use. | Those that receive power at low voltage are general electric facilities even if small output power generation facilities are installed on the same premises. | Even if it receives power at low voltage, it may not be an electric facility for general use depending on the place where it is installed, such as a business site where explosives are manufactured. | Those that receive high-voltage power are not general-purpose electric facilities, regardless of the capacity of the received power and the type of industry in which the demand is made. | 1 | ['電気工(でんきこう)- Electrician', '容量(ようりょう)- Capacity', '発電(はつでん)- Electricity generation', '構内(こうない)- Premises', '出力(しゅつりょく)- Output', '記述(きじゅつ)- Description', '作物(さくもつ)- Produce'] | 一般用{電気}工{作物}に関する{記述}として、誤っているものは。 | {低圧}で{受電}するもので、{出力}60kWの太陽{電池}{発電}{設備}を同一{構内}に{施設}するものは、一般用{電気}工{作物}となる。 | {低圧}で{受電}するものは、小{出力}{発電}{設備}を同一{構内}に{施設}しても一般用{電気}工{作物}となる。 | {低圧}で{受電}するものであっても、火薬類を{製造}する{事業}場など、{設置}する{場所}によっては一般用{電気}工{作物}とならない。 | {高圧}で{受電}するものは、{受電}{電力}の{容量}、{需要}{場所}の業{種}にかかわらず、一般用{電気}工{作物}とならない。 |  | 2019_1, 2018_1,
31 | What kind of equipment is the graphic symbol shown in ①? |  | Hook type outlet | Ceiling (directly attached to the ceiling) | Hook sealing (corner) | Embedded equipment | 3 | ['天井(てんじょう)- Ceiling', '器具(きぐ)- Instrument', '記号(きごう)- Sign'] | ①で{示す}{図}{記号}の{器具}の{種類}は。 | 引掛形{コンセント} | シーリング（{天井}直付） | 引掛シーリング（角） | 埋込{器具} |  | 2019_1,
32 | What is the minimum allowable value [MΩ] for the insulation resistance between the electric circuit and the ground in the part indicated by (2)? |  | 0.1 | 0.2 | 0.4 | 1 | 1 | ['最小値(さいしょうち)- Minimum value', '絶縁抵抗(ぜつえんていこう)- Insulation resistance', '部分(ぶぶん)- Portion'] | ②で{示す}{部分}の{電路}と{大地}間の{絶縁}抵抗として、{許容}される{最小}{値}［MΩ］は。 | 0.1 | 0.2 | 0.4 | 1 |  | 2019_1, 2017_2, 2016_1, 2015_2, 2015_1,
33 | What is the pole arrangement (blade support) of the outlet shown in ③? |  | Picture_33_A | Picture_33_B | Picture_33_C | Picture_33_D | 3 | ['配置(はいち)- Arrangement', '極(きょく)-Pole'] | ③で{示す}{コンセント}の{極}{配置}（刃受）は。 | Picture_33_A | Picture_33_B | Picture_33_C | Picture_33_D |  | 2019_1, 2016_1,
34 | What kind of equipment is the graphic symbol shown in ④? |  | Outlet with earth-leakage circuit breaker | Outlet with grounding electrode | Outlet with ground terminal | Outlet with grounding terminal with grounding electrode | 4 | ['接地(せっち)- ', '種類(しゅるい) -Type, Category'] | ④で{示す}{図}{記号}の{器具}の{種類}は。 | {漏電}{遮断器}付{コンセント} | {接地}{極}付{コンセント} | {接地}{端子}付{コンセント} | {接地}{極}付{接地}{端子}付{コンセント} |  | 2019_2, 2019_1, 2015_2,
35 | What is the purpose of using the equipment with the graphic symbol shown in ⑤? |  | Cut off the unbalanced current. | Cut off overcurrent and ground fault current. | Cut off only the ground fault current. | Cut off only the short-circuit current. | 4 | ['遮断(しゃだん)- Isolation', '目的(もくてき)- Purpose'] | ⑤で{示す}{図}{記号}の{器具}を用いる{目的}は。 | {不平衡}{電流}を{遮断}する。 | 過{電流}と地絡{電流}を{遮断}する。 | 地絡{電流}のみを{遮断}する。 | 短絡{電流}のみを{遮断}する。 |  | 2019_1,
36 | The maximum allowable value [Ω] of the grounding resistance in the grounding work of the part indicated by ⑥ is. |  | 10 | 100 | 300 | 500 | 4 | ['抵抗(ていこう)- Resistance', '最大値(さいだいち)- Global maximum', '部分(ぶぶん)- Portion'] | ⑥で{示す}{部分}の{接地}{工事}における{接地}抵抗の{許容}される{最大値}［Ω］は。 | 10 | 100 | 300 | 500 |  | 2019_1, 2016_1,
37 | What is the minimum number of wires (core wires) in the part indicated by ⑦? |  | 3 | 4 | 5 | 6 | 1 | ['本数(ほんすう)- Number ', '最少(さいしょう)- Lowest; minimum'] | ⑦で{示す}{部分}の{最少}{電線}{本数}（心線数）は。 | 3 | 4 | 5 | 6 |  | 2019_1, 2016_1,
38 | What is the minimum diameter [mm] of the conductor of the electric wire (annealed copper wire) that can be used in the small force circuit shown in ⑧? |  | 0.8 | 1.2 | 1.6 | 2 | 1 | ['回路(かいろ)- Circuit', '道(みち)- Road'] | ⑧で{示す}{部分}の小{勢力}{回路}で{使用}できる{電線}（軟{銅線}）の{導体}の{最小}{直径}［mm］は。 | 0.8 | 1.2 | 1.6 | 2 |  | 2019_1,
39 | The part indicated by ⑨ is the automatic flasher of the outdoor light. The side-by-side display of the graphic symbol. |  | A | T | P | L | 1 | ['表示(ひょうじ)- Indication', '自動(じどう)- Automatic', '部分(ぶぶん)- Section; Part'] | ⑨で{示す}{部分}は{屋外}灯の{自動}{点滅器}である。その{図}{記号}の傍記{表示}は。 | A | T | P | L |  | 2019_1, 2018_2,
40 | How to wire the graphic symbols shown in ⑩? |  | Ceiling concealed wiring | Floor concealment wiring | Exposed wiring | Lighting duct wiring | 2 | ['方法(ほうほう)- Method', '配線(はいせん)- Wiring'] | ⑩で{示す}{図}{記号}の{配線}{方法}は。 | {天井}隠ぺい{配線} | {床}隠ぺい{配線} | 露出{配線} | ライティングダクト{配線} |  | 2019_1, 2016_1,
41 | What is the equipment with the graphic symbol shown in ⑪? |  | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D | 3 | ['器具(きぐ)- Instrument'] | ⑪で{示す}{図}{記号}の{器具}は。 | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D |  | 2019_2, 2019_1, 2015_2,
42 | What is the equipment with the graphic symbol shown in ⑫? |  | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D | 4 | ['記号(きごう)- Symbol; code'] | ⑫で{示す}{図}{記号}の{器具}は。 | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D |  | 2019_1,
43 | What is the device with the graphic symbol shown in ⑬? |  | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D | 4 | ['機器(きき)- Device'] | ⑬で{示す}{図}{記号}の{機器}は。 | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D |  | 2019_1, 2015_2,
44 | If all the connections in the box shown in ⑭ are crimp connections, what is the correct combination of the type of ring sleep to be used and the minimum number? However, all wires used shall be VVF1.6. |  | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D | 2 | ['最少(さいしょう)- Lowest', '種類(しゅるい)- Variety', '圧着(あっちゃく)- Crimping', '接続(せつぞく)- Connection '] | ⑭で{示す}ボックス内の{接続}をすべて{圧着}{接続}とする{場合}、{使用}するリングスリープの{種類}と{最少}{個数}の{組合せ}で、{正しい}ものは。ただし、{使用}する{電線}は、すべてVVF1.6とする。 | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D |  | 2016_1, 2019_1,
45 | What is the device with the graphic symbol shown in ⑮? |  | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D | 3 | ['図(ず)- Picture; diagram'] | ⑮で{示す}{図}{記号}の{機器}は。 | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D |  | 2019_1,
46 | What is the correct tool for making holes for wiring in the wooden part shown in ⑯? |  | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D | 3 | ['示す(しめ)- To indicate'] | ⑯で{示す}{木造}{部分}に{配線}用の穴をあけるための{工具}として、{正しい}ものは。 | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D |  | 2019_1,
47 | If all the connections in the box shown in ⑰ are plug-in connectors, what is the correct combination of the type of plug-in connector to be used and the minimum number of connectors? However, all wires used shall be VVF1.6. |  | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D | 1 | ['電線(でんせん)- Cable', '種類(しゅるい)- Variety', '接続(せつぞく)- Connection '] | ⑰で{示す}ボックス内の{接続}をすべて差込形{コネクタ}とする{場合}、{使用}する差込形{コネクタ}の{種類}と{最少}{個数}の{組合せ}で、{正しい}ものは。ただし、{使用}する{電線}は、すべてVVF1.6とする。 | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D |  | 2019_1,
48 | What is the cable required for the wiring work of the part shown in ⑱? However, the number of core wires is the minimum. |  | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D | 2 | ['最少(さいしょう)- Lowest; Minimum', '必要(ひつよう)- Necessity'] | ⑱で{示す}{部分}の{配線}{工事}に{必要}なケーブルは。ただし、心線数は{最少}とする。 | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D |  | 2016_2, 2019_1,
49 | What is the equipment with the graphic symbol shown in ⑲? However, the figure below the photograph shows the configuration of the contacts. |  | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D | 2 | ['構成(こうせい)- Composition', '接点(せってん)- Tangent point', '記号(きごう)- Symbol; code'] | ⑲で{示す}{図}{記号}の{器具}は。ただし、{写真}下の{図}は、{接点}の{構成}を{示す}。 | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D |  | 2019_1, 2018_2,
50 | The correct tool for cutting the protective pipe (FEP) in the underground wiring work shown in ⑳ is |  | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D | 4 | ['正しい(ただ)- right; correct', '工具(こうぐ)- Hand tool', '地中(ちちゅう)- Underground;'] | ⑳で{示す}{地中}{配線}{工事}で{防護}{管}（FEP）を{切断}するための{工具}として、{正しい}ものは。 | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D |  | 2019_1,