## Sheet1
no | Eng | Picture | Option_1_Eng | Option_2_Eng | Option_3_Eng | Option_4_Eng | Ans | Vocab | Jpn | Option_1_Jpn | Option_2_Jpn | Option_3_Jpn | Option_4_Jpn | Exp | comment
1 | In the circuit shown in the figure, the combined resistance [Ω] between terminals a and b is. | Picture_1 | 1 | 2 | 3 | 4 | 2 | ['合成(ごうせい)- Combining', '端子(たんし)- Terminal', '回路(かいろ)- Circuit'] | {図}のような{回路}で、{端子}a - b間の{合成}抵抗［ Ω ］は。 | 1 | 2 | 3 | 4 | Parallel is (6x6)/(6+6)=3[Ω] 3[Ω]+3[Ω] =6[Ω] (3x6)/(3+6)=2[Ω]. | 2019_2,
2 | The copper conductor of the same material that has the closest resistance value to the copper conductor with a diameter of 2.6 mm and a length of 10 m. |  | Cross-sectional area 5.5 mm2, length 10 m | Cross-sectional area 8 mm2, length 10 m | Diameter 1.6 mm, length 20 m | Diameter 3.2 mm, length 5 m | 1 | ['材質(ざいしつ)- Material', '近い(ちか)- Near', '最も(もっと)- Most', '導線(どうせん)- Conducting wire'] | {直径}2.6 mm、{長さ}10 mの銅{導線}と抵抗{値}が最も近い同{材質}の銅{導線}は。 | Cross-sectional area 5.5 mm2, length 10 m | Cross-sectional area 8 mm2, length 10 m | Diameter 1.6 mm, length 20 m | Diameter 3.2 mm, length 5 m |  | 2019_2, 2018_2, 2016_2,
3 | What is the calorific value [kJ] when using an electric heater with power consumption of 500 W for 1 hour and 30 minutes? |  | 450 | 750 | 1800 | 2700 | 4 | ['消費電力(しょうひでんりょく)- Electricity consumption', '発熱量(はつねつりょう)- Calorific value'] | 消費{電力}が500 Wの{電熱器}を、１時間30分{使用}したときの{発熱量}［ kJ ］は。 | 450 | 750 | 1800 | 2700 | 1.5 x 60 x 60 = 5400s 500 x 5400 = 2700000 2,700,000 [J] = 2700 [kJ] | 2019_2, 2017_2,
4 | What is the correct waveform of the current i for the power supply voltage v of the sinusoidal AC circuit as shown in the figure? | Picture_4 | Picture_4_A | Picture_4_B | Picture_4_C | Picture_4_D | 3 | ['波形(はけい)- Waveform', '電源(でんげん)- Electrical power'] | {図}のような{正弦波}{交流}{回路}の{電源}{電圧} v に対する{電流} i の波形として、{正しい}ものは。 | Picture_4_A | Picture_4_B | Picture_4_C | Picture_4_D |  | 2019_2,
5 | What is the current I [A] flowing through the three-phase three-wire circuit as shown in the figure? | Picture_5 | 8.3 | 12.1 | 14.3 | 20 | 2 | ['電流(でんりゅう)- Electric current', '回路(かいろ)- Circuit', '三相(さんそう)- Three phases'] | {図}のような{三相}３{線}式{回路}に{流れる}{電流} I［ A ］は。 | 8.3 | 12.1 | 14.3 | 20 | Phase voltage =210/√3≒121.4(V) R = 121.4/10 ≒ 12.1(A). | 2019_2, 2018_2, 2015_2,
6 | In the single-phase three-wire circuit as shown in the figure, the two loads with power consumption of 100 W and 500 W are both resistance loads. If the wire is broken at the x mark in the figure, the voltage [V] between a and b is. However, it is assumed that the resistance value of the load does not change due to disconnection. | Picture_6 | 33 | 100 | 167 | 200 | 3 | ['断線(だんせん)- Disconnection', '場合(ばあい)- Case', '負荷(ふか)- Load'] | {図}のような{単相}３線式{回路}で、消費{電力}100 W、500 Wの２つの{負荷}はともに抵抗{負荷}である。{図}中の×印点で{断線}した{場合}、a - b 間の{電圧}［ V ］は。 ただし、{断線}によって{負荷}の抵抗{値}は変化しないものとする。 | 33 | 100 | 167 | 200 | I = 200÷120≒1.67 V = 1.67×100≒167 | 2019_2, 2016_1,
7 | In a three-phase three-wire circuit as shown in the figure, when the resistance per wire is 0.15 Ω and the wire current is 10 A, the voltage drop (Vs --Vr) [V] is. | Picture_7 | 1.5 | 2.6 | 3 | 4.5 | 2 | ['電線(でんせん)- Cable', '電圧降下(でんあつこうか)-Voltage Drop', '当たり(あ)- Hit'] | {図}のような{三相}３線式{回路}で、{電線}１線{当たり}の抵抗が0.15 Ω、線{電流}が10 Aのとき、{電圧}降下（ Vs - Vr ）［ V ］は。 | 1.5 | 2.6 | 3 | 4.5 | Voltage drop = √3 x load current x wire resistance Therefore, √3 x 10 [A] x 0.15 [Ω] ≒ 2.6 [V] | 2019_2,
8 | Allowable current per wire when three 600 V vinyl insulated wires (annealed copper wires) with a cross-sectional area of ​​5.5 mm2 are housed in the low-pressure indoor wiring work using synthetic resin flexible wire tubes (PF tubes). [A] is. However, the ambient temperature shall be 30 ° C or less, and the current reduction coefficient shall be 0.70. |  | 26 | 34 | 42 | 49 | 2 | ['減少(げんしょう)-Decrease', '周囲温度(しゅういおんど)- Ambient temperature', '許容(きょよう)- Acceptance', '絶縁(ぜつえん)- Insulation', '工事(こうじ)- Construction work', '屋内配線(おくないはいせん)- Interior wiring', '低圧(ていあつ)- Low voltage'] | {合成}樹脂製可とう{電線}管（PF管）による{低圧}{屋内配線}{工事}で、{管内}に{断面積}5.5 mm2の600 Vビニル{絶縁}{電線}（軟{銅線}）３本を収めて{施設}した{場合}、{電線}１本{当たり}の{許容}{電流}［ A ］は。 ただし、{周囲}{温度}は30°C{以下}、{電流}{減少}{係数}は0.70とする。 | 26 | 34 | 42 | 49 | the current reduction factor is 0.70, so 49 x 0.7 = 34.3 | 2019_2, 2016_1,
9 | When branching from a low-voltage indoor trunk line protected by an overcurrent circuit breaker with a rated current of 50 A as shown in the figure and installing an overcurrent circuit breaker at a position of 7 m, the minimum allowable current of the wire between a and b [A] is. | Picture_9 | 12.5 | 17.5 | 22.5 | 27.5 | 2 | ['最小値(さいしょうち)- Minimum value', '位置(いち)- Position (vector)', '分岐(ぶんき)- Divergence', '幹線(かんせん)- Main line', '屋内(おくない)- Indoor', '遮断器(しゃだんき)- Circuit breaker'] | {図}のように{定格}{電流}50 Aの過{電流}{遮断器}で保護された{低圧}{屋内}{幹線}から{分岐}して、７mの{位置}に過{電流}{遮断器}を{施設}するとき、a - b間の{電線}の{許容}{電流}の{最小}{値}[ A ]は。 | 12.5 | 17.5 | 22.5 | 27.5 | If the distance from the branch point to the overcurrent circuit breaker at the branch destination is 8m or less, the allowable current of the wire used for the branch circuit must be 35% or more of the rated current of the main line overcurrent circuit breaker. 50 x 0.35 = 17.5(A) | 2019_2, 2019_1, 2018_1, 2018_2, 2016_2, 2016_1, 2015_1, 2015_2,
10 | What is the appropriate combination of the thickness of the branch circuit wire (ampere wire) protected by the circuit breaker with a rated current of 30 A and the graphic symbol of the outlet that can be connected? However, the outlet shall not be a dual-purpose outlet. |  | Picture_10_A | Picture_10_B | Picture_10_C | Picture_10_D | 4 | ['適切(てきせつ)- Appropriate', '兼用(けんよう)- Multi-use', '記号(きごう)- Symbol', '電流(でんりゅう)- Electric current', '定格(ていかく)- Rated value'] | {定格}{電流}30 Aの{配線}用{遮断器}で保護される{分岐}{回路}の{電線}（軟{銅線}）の太さと、{接続}できる{コンセント}の{図}{記号}の{組合せ}として、{適切}なものは。ただし、{コンセント}は{兼用}{コンセント}ではないものとする。 | Picture_10_A | Picture_10_B | Picture_10_C | Picture_10_D | For the rated current of 30A, the following conditions are specified. ・Diameter 2.6mm or more ・Cross-sectional area 5.5m㎡ or more ・Outlet current 20A or more, 30A or less | 2019_2, 2017_2, 2016_2, 2016_1, 2015_2, 2015_1,
11 | What is the most suitable outlet for an electric dishwasher used in a house? |  | Hook-type outlet | Anti-removal type outlet | Outlet with grounding terminal | Outlet with grounding terminal | 4 | ['接地(せっち)- Ground (electricity)', '住宅(じゅうたく)- Residential building'] | {住宅}で{使用}する{電気}食器洗い機用の{コンセント}として、最も適しているものは。 | 引掛形{コンセント} | 抜け止め形{コンセント} | {接地}{端子}付{コンセント} | {接地}{極}付{接地}{端子}付コンセン |  | 2019_2,
12 | What is the highest allowable temperature for insulation? |  | 600 V Type 2 Vinyl Insulated Wire (HIV) | 600 V Vinyl Insulated Wire (IV) | 600 V Cross-Linked Polyethylene Insulated Vinyl Sheath Cable (CV) | 600 V Vinyl Insulated Vinyl Sheath Cable Round (VVR) | 3 | ['円形(えんけい)- Round shape', '架橋(かきょう)-Cross-link', '温度(おんど)- Temperature', '最高(さいこう)-highest'] | {絶縁}{物の}最高{許容}{温度}が最も{高い}ものは。 | 600 V 二{種}ビニル{絶縁}{電線}（HIV） | 600 V ビニル{絶縁}{電線}（IV） | 600 V {架橋}ポリエチレン{絶縁}ビニルシースケーブル（CV） | 600 V ビニル{絶縁}ビニルシースケーブル丸形（VVR） |  | 2019_2,
13 | What is the appropriate knockout puncher application? |  | Used to make holes in metal cabinets. | Used when crimping a thick wire. | Used to make holes in concrete walls. | Used to bend thick conduits. | 1 | ['圧着(あっちゃく)- Crimping', '適切(てきせつ)- Appropriate', '用途(ようと)- Use'] | ノックアウトパンチャの{用途}で、{適切}なものは。 | {金属}製キャビネットに穴を開けるのに用いる。 | {太い}{電線}を{圧着}{接続}する{場合}に用いる。 | コンクリート{壁}に穴を開けるのに用いる。 | {太い}{電線}{管}を曲げるのに用いる。 |  | 2019_2, 2015_2,
14 | In starting a three-phase induction motor, what are the correct characteristics of star-delta starting compared to full-voltage starting (starting directly)? |  | The starting time is shortened. | The starting current becomes smaller. | The starting torque increases. | The voltage applied to the winding at start-up increases. | 2 | ['電圧(でんあつ)- Voltage', '巻線(まきせん)- Winding', '特徴(とくちょう)- Feature', '比較(ひかく)- Comparison', '始動(しどう)-Starting'] | {三相}{誘導電動機}の{始動}において、全{電圧}{始動}（じか入れ{始動}）と{比較}して、スターデルタ{始動}の特徴として、{正しい}ものは。 | {始動}時間が短くなる。 | {始動}{電流}が小さくなる。 | {始動}トルクが大きくなる。 | {始動}時の巻{線}に加わる{電圧}が大きくなる。 |  | 2019_2,
15 | What is the limit of the time [minutes] that this circuit breaker must operate automatically when a current of 60 A continues to flow through the circuit breaker with a rated current of 30 A used for low piezoelectric paths? |  | 1 | 2 | 3 | 4 | 2 | ['限度(げんど)- Limit', '継続(けいぞく)- Continuation', '電流(でんりゅう)- Electric current', '定格(ていかく)- Rated value'] | {低圧}{電路}に{使用}する{定格}{電流}30 Aの{配線}用{遮断器}に60 Aの{電流}が{継続}して流れたとき、この{配線}用{遮断器}が{自動}的に動作しなければならない時間［ 分 ］の{限度}は。 | 1 | 2 | 3 | 4 |  | 2019_2,
16 | What is the name of the material shown in the photo? | Picture_16 | Bare crimping sleeve for copper wire | Copper tube terminal | Bare crimping terminal for copper wire | Screw-in type connector | 3 | ['圧着(あっちゃく)- Crimping', '名称(めいしょう)- Name', '材料(ざいりょう)- Materials'] | {写真}に{示す}{材料}の{名称}は。 {問題}{文}の{画像} | {銅線}用裸{圧着}スリーブ | 銅{管}{端子} | {銅線}用裸{圧着}{端子} | ねじ込み形{コネクタ} |  | 2019_2,
17 | What is the name of the equipment shown in the photo? | Picture_17 | Electric energy meter | Dimmer | Automatic flasher | Time switch | 4 | ['調光器(ちょうこうき)- Dimmer', '点滅器(てんめつき)- Flasher unit'] | {写真}に{示す}{器具}の{名称}は。 {問題}{文}の{画像} | {電力}量計 | {調光器} | {自動}{点滅器} | タイム{スイッチ} |  | 2019_2,
18 | What are the uses of the tools shown in the photo? | Picture_18 | Used to peel off the exterior and insulation coating of VVF cables. | Used to peel off the exterior and insulation coating of CV cables (for low voltage). | Used to peel off the exterior and insulation coating of VVR cables. | Used to remove the insulation coating of VFF cord (vinyl flat cord) | 1 | ['絶縁(ぜつえん)- Insulation', '被覆(ひふく)- Coating', '外装(がいそう)- Exterior'] | {写真}に{示す}{工具}の{用途}は。 {問題}{文}の{画像} | VVFケーブルの{外装}や{絶縁}{被覆}をはぎ取るのに用いる。 | CVケーブル（{低圧}用）の{外装}や{絶縁}{被覆}をはぎ取るのに用いる。 | VVRケーブルの{外装}や{絶縁}{被覆}をはぎ取るのに用いる。 | VFFコード（ビニル平形コード）の{絶縁}{被覆}をはぎ取るのに用いる。 |  | 2019_2, 2018_2, 2016_2,
19 | In the low-voltage indoor wiring work, 600 V vinyl insulated wire (anhydrous copper wire) was terminated and connected using a crimping tool for ring sleeve and ring sleeve (E type). What is the wrong combination of ring sleeve type and crimping mark (engraved) that matches the wire to be connected? |  | With a diameter of 2.0 mm, a crimping mark was placed inside using a middle sleeve for connecting three pieces. | A small sleeve was used to make the crimping mark small for connecting three pieces with a diameter of 1.6 mm. | 2.0 mm in diameter A crimping mark was placed inside using a middle sleeve for connecting two pieces. | A crimping mark was placed inside using a middle sleeve to connect one 1.6 mm diameter and two 2.0 mm diameter. | 3 | ['圧着(あっちゃく)-Crimping', '直径(ちょっけい)- Diameter', '刻印(こくいん)- Engraving a seal', '種類(しゅるい)- Type', '接続(せつぞく)- Connection', '低圧(ていあつ)- Low voltage'] | {低圧}{屋内配線}{工事}で、600 Vビニル{絶縁}{電線}（軟{銅線}）をリングスリーブ用{圧着}{工具}とリングスリーブ（E 形）を用いて{終端}{接続}を行った。{接続}する{電線}に適合するリングスリーブの{種類}と{圧着}マーク（{刻印}）の{組合せ}で、{不適切}なものは。 | {直径}2.0 mm ３本の{接続}に、中スリーブを{使用}して{圧着}マークを中にした。 | {直径}1.6 mm ３本の{接続}に、小スリーブを{使用}して{圧着}マークを小にした。 | {直径}2.0 mm ２本の{接続}に、中スリーブを{使用}して{圧着}マークを中にした。 | {直径}1.6 mm １本と{直径}2.0 mm ２本の{接続}に、中スリーブを{使用}して{圧着}マークを中にした。 |  | 2019_2, 2018_1, 2015_1,
20 | What is the inappropriate type of construction work at the facility location for indoor wiring with a working voltage of 100 V? |  | Lighting duct construction in a dry place, a hidden place that cannot be inspected | Synthetic resin pipe construction (excluding CD pipes) with a moisture-proof device in a concealed place that cannot be inspected and in a humid place | Cable construction in a place where it was deployed and where there is a lot of humidity | Metal pipe construction with a moisture-proof device in a place where it has been deployed and where there is a lot of humidity. | 1 | ['防湿(ぼうしつ)-Damp proofing', '装置(そうち)- Equipment', '湿気(しっけ)- Humidity', '隠蔽(いんぺい)- Concealment'] | {使用}{電圧}100 Vの{屋内配線}の{施設}{場所}における{工事}の{種類}で、{不適切}なものは。 | {点検}できない隠ぺい{場所}であって、乾燥した{場所}のライティングダクト{工事} | {点検}できない隠ぺい{場所}であって、{湿気}の多い{場所}の{防湿}装置を施した{合成}樹脂{管}{工事}（CD{管}を除く） | 展開した{場所}であって、{湿気}の多い{場所}のケーブル{工事} | 展開した{場所}であって、{湿気}の多い{場所}の{防湿}装置を施した{金属}{管}{工事} |  | 2019_2, 2017_1, 2015_1,
21 | What is the inappropriate construction method for single-phase three-wire 100/200 V indoor wiring work in a wooden house? However, the wire used shall be a 600 V vinyl insulated wire and a diameter of 1.6 mm (annealed copper wire). |  | Flexible conduits made of synthetic resin (CD pipes) were piped under the wooden floor, inside the walls, and behind the ceiling. | A flexible wire tube (PF tube) made of synthetic resin was passed through, and the distance between the support points was fixed to the building material at 1.0 m. | Two rigid vinyl chloride conduits (VE) of the same diameter were connected by TS coupling. | Used in a concealed place where the metal pipe cannot be inspected. | 1 | ['床下(ゆかした)- Under the floor', '方法(ほうほう)- Method', '木造(もくぞう)- Made of wood', '直径(ちょっけい)- Diameter', '木造住宅(もくぞうじゅうたく)- Wooden house'] | {木造}{住宅}の{単相}３線式100 / 200 V{屋内配線}{工事}で、{不適切}な{工事}{方法}は。ただし、{使用}する{電線}は600 Vビニル{絶縁}{電線}、{直径}1.6 mm（軟{銅線}）とする。 | {合成}樹脂製可とう{電線}{管}（CD{管}）を{木造}の{床}下や{壁}の{内部}及び{天井}裏に配{管}した。 | {合成}樹脂製可とう{電線}{管}（PF{管}）内に通線し、支持点間の{距離}を1.0 mで造営材に固定した。 | {同じ}径の{硬質}塩化ビニル{電線}{管}（VE）２本をTSカップリングで{接続}した。 | {金属}{管}を{点検}できない隠ぺい{場所}で{使用}した。 |  | 2019_2, 2018_2, 2015_2,
22 | What cannot omit the D-class grounding work? However, it is assumed that the electric circuit is equipped with an earth-leakage circuit breaker with a rated sensitivity current of 30 mA and a rated operating time of 0.1 seconds. |  | A 3m long metal tube containing electric wires for three-phase 200 V (voltage to ground 200 V) power wiring installed in a dry place. | A 6 m long metal tube containing electric wires for single-phase three-wire 100/200 V (voltage to ground 100 V) wiring installed in a dry place. | Metal outer box part of a three-phase 200 V (to-ground voltage 200 V) air compressor to be handled on a dry wooden floor. | The iron stand of a three-phase 200 V (voltage to ground 200 V) induction motor installed on a concrete floor in a dry place. | 4 | ['誘導電動機(ゆうどうでんどうき)- Induction motor', '感度(かんど)- Sensitivity ', '省略(しょうりゃく)- Omission', '種(たね)- Seed'] | D{種}{接地}{工事}を{省略}できないものは。ただし、{電路}には{定格}{感度}{電流}30 mA、{定格}{動作時間}0.1 秒の{漏電}{遮断器}が取り付けられているものとする。 | 乾燥した{場所}に{施設}する{三相}200 V（{対地}{電圧}200 V）動力{配線}の{電線}を収めた{長さ}３mの{金属}{管}。 | 乾燥した{場所}に{施設}する{単相}３線式100 / 200 V（{対地}{電圧}100 V）{配線}の{電線}を収めた{長さ}６mの{金属}{管}。 | 乾燥した木製の{床}の上で取り扱うように{施設}する{三相}200 V（{対地}{電圧}200 V）空気{圧縮機}の{金属}製{外箱}{部分}。 | 乾燥した{場所}のコンクリートの{床}に{施設}する{三相}200 V（{対地}{電圧}200 V）{誘導電動機}の鉄台。 |  | 2019_2, 2018_1, 2015_2,
23 | What is the appropriate way to insert an electric wire into a metal tube so as not to cause an electromagnetic imbalance? |  | Picture_23_A | Picture_23_B | Picture_23_C | Picture_23_D | 2 | ['適切(てきせつ)- Appropriate', '不平衡(ふへいこう)- Imbalance', '電磁的(でんじてき)- Electromagnetic'] | {電磁}的{不平衡}を生じないように、{電線}を{金属}{管}に挿入する{方法}として、{適切}なものは。 | Picture_23_A | Picture_23_B | Picture_23_C | Picture_23_D |  | 2019_2, 2016_2,
24 | When inspecting indoor wiring, what is the inappropriate way to use the equipment? |  | Check with a voltage detector to see if there is charging. | Measure the ground resistance with a ground resistance meter (earth tester). | Measure the amount of power with a circuit meter (tester). | Measure the insulation resistance with an insulation resistance tester (megger). | 3 | ['有無(うむ)- ', '充電(じゅうでん)- Charging ', '検電器(けんでんき)- Voltage detector'] | {屋内配線}の{検査}を行う{場合}、{器具}の{使用}{方法}で、{不適切}なものは。 | {検電器}で{充電}の有無を{確認}する。 | {接地}抵抗計（{アース}テスタ）で{接地}抵抗を{測定}する。 | {回路}計（テスタ）で{電力}量を{測定}する。 | {絶縁}抵抗計（メガー）で{絶縁}抵抗を{測定}する。 |  | 2019_2,
25 | What is the appropriate method to open the branch switch, completely separate the load from the power supply, and measure the insulation resistance between the low-voltage indoor circuit on the load side and the ground all at once? |  | Turn off all flashers on the load side, and measure the load that is always connected to the wiring while it is still in use. | Turn off all flashers on the load side, and remove all loads that are always connected to the wiring before measuring. | Turn on all the flashers on the load side, and measure the load that is always connected to the wiring while it is still in use. | Turn on all the flashers on the load side, and remove all the loads that are always connected to the wiring before measuring. | 3 | ['入り(い)- Entering', '常時(じょうじ)- Always', '状態(じょうたい)- Situation', '開閉器(かいへいき)- Switch', '分岐(ぶんき)- Divergence'] | {分岐}{開閉器}を{開放}して{負荷}を{電源}から完全に分離し、その{負荷}側の{低圧}{屋内}{電路}と{大地}間の{絶縁}抵抗を一括{測定}する{方法}として、{適切}なものは。 | {負荷}側の{点滅器}をすべて「切」にして、{常時}{配線}に{接続}されている{負荷}は、{使用}{状態}にしたままで{測定}する。 | {負荷}側の{点滅器}をすべて「切」にして、{常時}{配線}に{接続}されている{負荷}は、すべて取り外して{測定}する。 | {負荷}側の{点滅器}をすべて「入」にして、{常時}{配線}に{接続}されている{負荷}は、{使用}{状態}にしたままで{測定}する。 | {負荷}側の{点滅器}をすべて「入」にして、{常時}{配線}に{接続}されている{負荷}は、すべて取り外して{測定}する。 |  | 2019_2, 2016_1,
26 | What is the correct combination that applies to the following blanks (A), (B) and (C)? The insulation resistance between the wires of low-voltage electric circuits whose working voltage exceeds 300 V and between the electric circuit and the ground must be (A) [MΩ] or more for each electric circuit that can be separated. In addition, it is necessary to perform (B) grounding work on the metal base and outer box of the machinery and equipment installed in the electric circuit, and to install the grounding resistance value below (C) [Ω]. However, the operating time of the ground fault breaker installed in the electric circuit shall exceed 0.5 seconds. |  | A：0.4 B：C種 C：10 | A：0.4 B：C種 C：500 | A：0.2 B：D種 C：100 | A：0.4 B：D種 C：500 | 1 | ['遮断(しゃだん)- Isolation', '当該(とうがい)- Appropriate', '大地(だいち)- Ground', '電路(でんろ)-Electrical circuit', '低圧(ていあつ)- Low pressure '] | 次の空欄（ A ）、（ B ）及び（ C ）に当てはまる{組合せ}として、{正しい}ものは。 {使用}{電圧}が300 Vを超える{低圧}の{電路}の{電線}{相互}間及び{電路}と{大地}との間の{絶縁}抵抗は区切ることのできる{電路}ごとに（ A ）［ MΩ ］以上でなければならない。また、当該{電路}に{施設}する{機械}{器具}の{金属}製の台及び{外箱}には（ B ）{接地}{工事}を施し、{接地}抵抗{値}は、（ C ）［ Ω ］{以下}に{施設}することが{必要}である。 ただし、当該{電路}に{施設}された地絡{遮断}装置の{動作時間}は0.5 秒を超えるものとする。 | A：0.4 B：C{種} C：10 | A：0.4 B：C{種} C：500 | A：0.2 B：D{種} C：100 | A：0.4 B：D{種} C：500 |  | 2019_2,
27 | The AC circuit in the figure is a circuit that measures the voltage, current, and power of the load. What is the correct combination of instruments indicated by a, b, and c in the figure? |  | a: Ammeter b: Voltmeter c: Wattmeter | a: Power meter b: Ammeter c: Voltmeter | a: Voltmeter b: Wattmeter c: Ammeter | a: Voltmeter b: Ammeter c: Wattmeter | 4 | ['計器(けいき)- Meter', '電圧(でんあつ)- Voltage'] | {図}の{交流}{回路}は、{負荷}の{電圧}、{電流}、{電力}を{測定}する{回路}である。{図}中にa、b、cで{示す}{計器}の{組合せ}として、{正しい}ものは。 | a：{電流}計 b：{電圧}計 c：{電力}計 | a：{電力}計 b：{電流}計 c：{電圧}計 | a：{電圧}計 b：{電力}計 c：{電流}計 | a：{電圧}計 b：{電流}計 c：{電力}計 |  | 2019_2, 2017_1,
28 | Under the Electricians Act, what is the construction or work of general electric facilities that can only be engaged by an electrician? |  | Wire the secondary side of the small transformer (secondary voltage is 36 V or less) used in the interhorn facility. | Install pillars and arms to support electric wires. | Install a watt-hour meter for use with a voltage of 600 V or less. | Connect the conduit and the box. | 4 | ['電線(でんせん)- Cable', '変圧器(へんあつき)- Transformer', '小型(こがた)- Small', '作業(さぎょう)- Work'] | {電気}{工事}士法において、一般用{電気}工{作物}の{工事}又は{作業}で{電気}{工事}士でなければ{従事}できないものは。 | インターホーンの{施設}に{使用}する{小型}{変圧器}（二次{電圧}が36 V{以下}）の二次側の{配線}をする。 | {電線}を支持する柱、{腕木}を{設置}する。 | {電圧}600 V{以下}で{使用}する{電力}量計を取り付ける。 | {電線}{管}とボックスを{接続}する。 |  | 2019_2,
29 | What is wrong with the description of electrical appliances in the Electrical Appliance and Material Safety Law? |  | A person who manufactures or imports electrical appliances may attach a label by the method specified by the Ordinance of the Ministry of Economy, Trade and Industry when he / she fulfills the obligations stipulated in the Electrical Appliance and Material Safety Law. | Specified electrical appliances are electrical appliances that are particularly likely to cause danger or failure in view of their structure, usage, and other usage conditions, and are specified by Cabinet Order. | Specified electrical equpment is labeled with (PSE) or (PS)E. | An electrician shall not use electrical equipment that is not labeled as stipulated in the Electrical Appliance and Material Safety Law for the installation or modification of electric facilities. | 3 | ['設置(せっち)- Installation', '障害(しょうがい)- Obstacle', '構造(こうぞう)- Structure', '特定(とくてい)- Specific', '方式(ほうしき)- Method', '事業(じぎょう)- Project', '用品(ようひん)- Equipment'] | {電気}{用品}安全法における{電気}{用品}に関する{記述}として、誤っているものは。 | {電気}{用品}の{製造}又は{輸入}の{事業}を行う者は、{電気}{用品}安全法に規定する{義務}を履行したときに、経済産業{省令}で定める{方式}による{表示}を付すことができる。 | {特定}{電気}{用品}は{構造}又は{使用}{方法}その他の{使用}状況からみて特に{危険}又は{障害}の{発生}するおそれが多い{電気}{用品}であって、政令で定めるものである。 | {特定}{電気}{用品}には(PS)Eの{表示}が付されている。 | {電気}{工事}士は、{電気}{用品}安全法に規定する{表示}の付されていない{電気}{用品}を{電気}工{作物}の{設置}又は変更の{工事}に{使用}してはならない。 |  | 2019_2, 2019_1, 2018_1,
30 | What is the correct combination of low voltage classifications in the "Ministry Ordinance that Establishes Technical Standards for Electrical Equipment"? |  | AC 600 V or less, DC 750 V or less | AC 600 V or less, DC 700 V or less | AC 600 V or less, DC 600 V or less | AC 750 V or less, DC 600 V or less | 1 | ['直流(ちょくりゅう)- Direct current', '以下(いか)- Below ', '省令(しょうれい)- Ministerial ordinance', '変更(へんこう)-Change'] | 「{電気}{設備}に関する{技術基準}を定める{省令}」における{電圧}の{低圧}区分の{組合せ}で、{正しい}ものは。 | {交流}600 V{以下}、{直流}750 V{以下} | {交流}600 V{以下}、{直流}700 V{以下} | {交流}600 V{以下}、{直流}600 V{以下} | {交流}750 V{以下}、{直流}600 V{以下} |  | 2019_2, 2018_2, 2017_2,
31 | What is the purpose of using the instrument with the graphic symbol shown in ①? |  | Measure the load factor. | Measure power. | Measure the amount of electricity. | Measure maximum power. | 3 | ['最大(さいだい)- Maximum', '測定(そくてい)- Measurement', '電力量(でんりょくりょう)- Electric energy', '負荷率(ふかりつ)- Load factor'] | ①で{示す}{図}{記号}の{計器}の{使用}{目的}は。 | {負荷}率を{測定}する。 | {電力}を{測定}する。 | {電力}量を{測定}する。 | 最大{電力}を{測定}する。 |  | 2019_2, 2015_1,
32 | What is the maximum voltage [V] that can be used in the small power circuit shown in (2)? |  | 24 | 30 | 40 | 60 | 4 | ['最大値(さいだいち)- Greatest value', '勢力(せいりょく)-Power', '部分(ぶぶん)- Part'] | ②で{示す}{部分}の小{勢力}{回路}で{使用}できる{電圧}の{最大値}［ V ］は。 | 24 | 30 | 40 | 60 |  | 2019_2,
33 | What kind of equipment is the graphic symbol shown in ③? |  | Flasher with built-in position indicator | Flasher with built-in confirmation indicator | Delay switch | Hot wire type automatic switch | 2 | ['確認(かくにん)- Confirmation; check', '点滅器(てんめつき)- Flasher unit', '表示灯(ひょうじとう)- Signal light'] | ③で{示す}{図}{記号}の{器具}の{種類}は。 | {位置}{表示}灯を内蔵する{点滅器} | {確認}{表示}灯を内蔵する{点滅器} | {遅延}{スイッチ} | 熱{線}式{自動}{スイッチ} |  | 2019_2, 2017_2,
| What kind of equipment is the graphic symbol shown in ④? |  | Outlet with ground terminal | Outlet with grounding terminal with grounding electrode | Outlet with grounding electrode | With grounding electrode With grounding terminal With earth-leakage circuit breaker Outlet | 4 | ['接地(せっち)- Ground (electricity)'] | ④で{示す}{図}{記号}の{器具}の{種類}は | {接地}{端子}付{コンセント} | {接地}{極}付{接地}{端子}付{コンセント} | {接地}{極}付{コンセント} | {接地}{極}付{接地}{端子}付{漏電}{遮断器}付{コンセント} |  | 2019_2, 2019_1, 2015_2,
35 | I want to attach a pendant to the part indicated by ⑤. The graphic symbol is. |  | Picture_35_A | Picture_35_B | Picture_35_C | Picture_35_D | 3 | ['部分(ぶぶん)- Section; part', '示す(しめ)- To indicate'] | ⑤で{示す}{部分}にペンダントを取り付けたい。{図}{記号}は。 | Picture_35_A | Picture_35_B | Picture_35_C | Picture_35_D |  | 2019_2,
36 | The part indicated by ⑥ is the indoor unit of the room air conditioner. The side-by-side display of the graphic symbol is |  | O | R | B | I | 4 | ['表示(ひょうじ)- Indication', '記号(きごう) -Symbol', '屋内(おくない)- Indoor'] | ⑥で{示す}{部分}はルームエアコンの{屋内}ユニットである。その{図}{記号}の傍記{表示}は。 | O | R | B | I |  | 2019_2, 2017_2, 2015_1,
37 | What is the pole arrangement (blade support) of the outlet shown in ⑦? |  | Picture_37_A | Picture_37_B | Picture_37_C | Picture_37_D | 1 | ['配置(はいち)- Arrangement', '極(きょく)- Pole'] | ⑦で{示す}{コンセント}の{極}{配置}（刃受）は。 | Picture_37_A | Picture_37_B | Picture_37_C | Picture_37_D |  | 2019_2,
38 | What is the minimum number of wires (core wires) in the part indicated by ⑧? |  | 2 | 3 | 4 | 5 | 2 | ['本数(ほんすう)- Number', '最少(さいしょう)- Lowest; Minimum'] | ⑧で{示す}{部分}の{最少}{電線}{本数}（心線数）は。 | 2 | 3 | 4 | 5 |  | 2019_2,
39 | The minimum allowable value [MΩ] for the insulation resistance between the electric circuit and the ground in the part indicated by ⑨ is |  | 0.1 | 0.2 | 0.4 | 1 | 1 | ['大(だい)- Large', '最小値(さいしょうち)- Minimum value', '絶縁抵抗(ぜつえんていこう)- Insulation resistance'] | ⑨で{示す}{部分}の{電路}と{大地}間の{絶縁}抵抗として、{許容}される{最小}{値}［ MΩ ］は。 | 0.1 | 0.2 | 0.4 | 1 |  | 2019_2, 2018_2,
40 | What kind of equipment is the graphic symbol shown in ⑩? |  | Ceiling (directly attached to the ceiling) | Hook ceiling (round) | Embedded equipment | Ceiling outlet (hook type) | 3 | ['天井(てんじょう)- Ceiling', '種類(しゅるい)- Variety'] | ⑩で{示す}{図}{記号}の{器具}の{種類}は。 | シーリング（{天井}直付） | 引掛シーリング（丸） | 埋込{器具} | {天井}{コンセント}（引掛形) |  | 2019_2,
41 | If all the connections in the box shown in ⑪ are crimp connections, what is the correct combination of the type of ring sleeve to be used and the minimum number? However, all wires used shall be VVF 1.6. |  | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D | 1 | ['電線(でんせん)- Cable', '種類(しゅるい)- Variety, Type', '場合(ばあい)- Case; Situation', '接続(せつぞく)- Connection'] | ⑪で{示す}ボックス内の{接続}をすべて{圧着}{接続}とする{場合}、{使用}するリングスリーブの{種類}と{最少}{個数}の{組合せ}で、{正しい}ものは。ただし、{使用}する{電線}はすべてVVF 1.6とする。 | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D |  | 2019_2,
42 | What is the cable used for the wiring work of the part indicated by ⑫? However, the number of core wires is the minimum. |  | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D | 2 | ['最少(さいしょう)- Lowest; Minimum', '部分(ぶぶん)- Section; Part'] | ⑫で{示す}{部分}の{配線}{工事}に{使用}するケーブルは。ただし、心線数は{最少}とする。 | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D |  | 2019_2,
43 | What is the equipment with the graphic symbol shown in ⑬? |  | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D | 4 | ['器具(きぐ)- Instrument; appliance;', '記号(きごう)-Sign (semiotics)'] | ⑬で{示す}{図}{記号}の{器具}は。 | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D |  | 2019_2,
44 | What equipment is attached to the part indicated by ⑭? |  | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D | 3 | ['機器(きき)- Equipment', '部分(ぶぶん)- Section; Part'] | ⑭で{示す}{部分}に取り付ける{機器}は。 | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D |  | 2019_2,
45 | What measures the load current of the circuit shown in ⑮? |  | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D | 4 | ['電流(でんりゅう)- Electric current', '回路(かいろ)- Circuit'] | ⑮で{示す}{回路}の{負荷}{電流}を{測定}するものは。 | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D |  | 2019_2,
46 | What is the equipment with the graphic symbol shown in ⑯? |  | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D | 2 | ['記号(きごう)- Code; sign', '器具(きぐ)- Instrument; appliance'] | ⑯で{示す}{図}{記号}の{器具}は。 | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D |  | 2019_2,
47 | What is the correct combination of markings after crimping when the connection inside the box shown in ⑰ is crimped using three small ring sleeves? However, all wires used shall be VVF 1.6. In addition, O and small in the center of the ring sleeve shown in the photograph indicate the engraving. |  | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D | 1 | ['電線(でんせん)- Cable', '刻印(こくいん)- Engraving a seal', '場合(ばあい)- Case; Situation', '圧着(あっちゃく)- Crimping; Pressure bonding', '接続(せつぞく)- Connection'] | ⑰で{示す}ボックス内の{接続}をリングスリーブ小３個を{使用}して{圧着}{接続}した{場合}の{圧着}{接続}後の{刻印}の{組合せ}で、{正しい}ものは。ただし、{使用}する{電線}はすべてVVF 1.6とする。また、{写真}に{示す}リングスリーブ{中央}のO、小は{刻印}を表す。 | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D |  | 2019_2,
48 | What is the graphic symbol shown in ⑱? |  | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D | 1 | ['図(ず)- Picture; Diagram; Figure'] | ⑱で{示す}{図}{記号}のものは。 | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D |  | 2019_2, 2019_1, 2015_2,
49 | If all the connections in the box shown in ⑲ are plug-in connectors, what is the correct combination of the type of plug-in connector to be used and the minimum number of connectors? However, all wires used shall be VVF 1.6. |  | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D | 4 | ['電線(でんせん)- Cable', '個数(こすう)- Quantity', '種類(しゅるい)- Type; Category', '接続(せつぞく)- Connection '] | ⑲で{示す}ボックス内の{接続}をすべて差込形{コネクタ}とする{場合}、{使用}する差込形{コネクタ}の{種類}と{最少}{個数}の{組合せ}で、{正しい}ものは。ただし、{使用}する{電線}はすべてVVF 1.6とする。 | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D |  | 2019_2,
50 | Switches not used in the graphic symbols in this wiring diagram. However, the figure below the photo shows the contact configuration. |  | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D | 3 | ['接点(せってん)- Tangent point', '記号(きごう)- Sign', '配線図(はいせんず)- Wiring diagram'] | この{配線}{図}の{図}{記号}で{使用}されていない{スイッチ}は。ただし、{写真}下の{図}は、{接点}の{構成}を{示す}。 | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D |  | 2019_2, 2017_2, 2016_1, 2015_2,