## Sheet1
no | Eng | Picture | Option_1_Eng | Option_2_Eng | Option_3_Eng | Option_4_Eng | Ans | Vocab | Jpn | Option_1_Jpn | Option_2_Jpn | Option_3_Jpn | Option_4_Jpn | Exp | comment
1 | What is the current I [A] flowing through the DC circuit as shown in the figure? | Picture_1 | 1 | 2 | 4 | 8 | 3 | ['流れる(なが)- To flow', '直流回路(ちょくりゅうかいろ)- Direct-Current Circuit'] | {図}のような{直流}{回路}に{流れる}{電流}I［A］は。 | 1 | 2 | 4 | 8 | R = (4×4)/(4+4) = 2Ω Rt = =2+2 = 4Ω. | 2020_1,
2 | There are two copper wires of the same material, A and B. A is 1.6 mm in diameter and 20 m long, and B is 3.2 mm in diameter and 40 m long. How many times the resistance of A is the resistance of B? |  | 2 | 3 | 4 | 5 | 1 | ['抵抗(ていこう)- Resistance', '長さ(なが)- Length', '直径(ちょっけい)- Diameter', '材質(ざいしつ)- Material'] | A、B2本の同{材質}の{銅線}がある。Aは{直径}1.6mm、{長さ}20m、Bは{直径}3.2mm、{長さ}40mである。Aの抵抗はBの抵抗の何倍か。 | 2 | 3 | 4 | 5 |  | 2020_1,
3 | Due to poor wire connection, the contact resistance at the connection point was 0.2Ω. When a current of 15A flows through this wire, the amount of heat [kJ] generated in one hour from the connection point is. However, the value of contact resistance should not change. |  | 11 | 45 | 72 | 162 | 4 | ['電流(でんりゅう)- Electric current', '接触(せっしょく)- Touch', '接続(せつぞく)-Connection', '電線(でんせん)- Electric cable'] | {電線}の{接続}{不良}により、{接続}点の{接触}抵抗が0.2Ωとなった。この{電線}に15Aの{電流}が{流れる}と、{接続}点から1時間に{発生}する{熱量}［kJ］は。 ただし、{接触}抵抗の{値}は変化しないものとする。 | 11 | 45 | 72 | 162 | 1 hour = 3600 seconds so substitute, = 15 x 15 ×0.2×3600 =162000 (J) =162 (kJ) | 2020_1,
4 | The formula that shows the power factor [%] of the AC circuit as shown in the figure. | Picture_2 | 100𝑅𝑋/(𝑅^2+𝑋^2 ) | 100R/√(𝑅^2+𝑋^2) | 100X/√(𝑅^2+𝑋^2) | 100X/R+X | 2 | ['力率(りきりつ)- Power factor', '交流(こうりゅう)- Alternating current; AC'] | {図}のような{交流}{回路}の{力率}［%］を{示す}式は。 | 100𝑅𝑋/(𝑅^2+𝑋^2 ) | 100R/√(𝑅^2+𝑋^2) | 100X/√(𝑅^2+𝑋^2) | 100X/R+X | DC component Vr=IR AC component Vz=I√(R^2+X^2) (^2...square power) Therefore IR/(I√(R^2+X^2))×100 100R/√(R^2+X^2) | 2020_1,
5 | When a three-phase induction motor with a rated voltage of V [V] and a rated current of I [A] was continuously operated for a period of time t [h] in the rated state, the power consumption was W [kW · h]. What is the formula for expressing the power factor [%] of this motor? |  | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D | 4 | ['状態(じょうたい)- State', '誘導電動機(ゆうどうでんどうき)- Induction motor', '電圧(でんあつ)- Voltage'] | {定格}{電圧}V［V］、{定格}{電流}I［A］の{三相}{誘導電動機}を{定格}{状態}で時間t［h］の間、連続運転したところ、消費{電力}量がW［kW・h］であった。この電動機の{力率}［%］を表す式は。 | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D |  | 2020_1,
6 | In a three-phase three-wire circuit as shown in the figure, when the resistance per wire is r [Ω] and the wire current is I [A], what is the formula for the power loss [W] in this wire line? | Picture_6 | √3I2r | 3Ir | 3I2r | √3Ir | 3 | ['電力損失(でんりょくそんしつ)- Electric power loss', '電流(でんりゅう)- Electric current', '回路(かいろ)- Circuit', '三相(さんそう)- Three phases'] | {図}のような{三相}3線式{回路}において、{電線}1線{当たり}の抵抗がr［Ω］、線{電流}がI［A］のとき、この{電線}路の{電力}損失［W］を{示す}式は | √3I2r | 3Ir | 3I2r | √3Ir |  | 2020_1,
7 | In a single-phase three-wire circuit as shown in the figure, when the resistance per wire is 0.1Ω and the current flowing through the resistor load is both 15A, the power loss [W] of this power line is. | Picture_7 | 45 | 60 | 90 | 135 | 1 | ['抵抗(ていこう)- esistance'] | {図}のような{単相}3線式{回路}において、{電線}1線{当たり}の抵抗が0.1Ω、抵抗{負荷}に{流れる}{電流}がともに15Aのとき、この{電線}路の{電力}損失［W］は。 | 45 | 60 | 90 | 135 | P=2×0.1×15^2 =45 | 2020_1,
8 | When installing four 600V vinyl insulated wires (annealed copper wires) with a cross-sectional area of ​​5.5 mm2 in a low-voltage indoor wiring work using metal pipes, what is the allowable current [A] per wire? However, the ambient temperature should be 30°C or less, and the current reduction factor should be 0.63. |  | 19 | 24 | 31 | 49 | 3 | ['電線(でんせん)- Electric cable', '銅線(どうせん)- Copper wire', '低圧(ていあつ)- Low voltage'] | {金属}管による{低圧}{屋内配線}{工事}で、{管内}に{断面積}5.5mm2の600Vビニル{絶縁}{電線}（軟{銅線}）4本を収めて{施設}した{場合}、{電線}1本{当たり}の{許容}{電流}［A］は。 ただし、{周囲}{温度}は30℃{以下}、{電流}{減少}{係数}は0.63とする。 | 19 | 24 | 31 | 49 | The allowable current value of a 600V vinyl insulated wire with a cross-sectional area of ​​5.5mm2 is 49A. So 49 x 0.63 = 31 | 2020_1,
9 | As shown in the figure, when a three-phase electric motor and electric heater are connected to a low-voltage indoor main line, what is the minimum current value [A] that determines the thickness of the main line? However, the demand rate is assumed to be 100%. | Picture_9 | 95 | 103 | 115 | 255 | 2 | ['電流(でんりゅう)- Electric current', '場合(ばあい)- Case; Situation', '低圧(ていあつ)- Low voltage', '電熱器(でんねつき)- Electrothermic equipment', '電動機(でんどうき)- Electric motor'] | {図}のように、{三相}の{電動機}と{電熱器}が{低圧}{屋内}{幹線}に{接続}されている{場合}、{幹線}の太さを決める{根拠}となる{電流}の{最小}{値}［A］は。 ただし、{需要}率は100%とする。 | 95 | 103 | 115 | 255 |  | 2020_1,
10 | In the design of branch circuits for low-voltage indoor wiring, what is the appropriate combination of circuit breakers, branch circuit wire thicknesses, and outlets? However, the distance from the branch point to the circuit breaker for wiring is 3 m, and the distance from the circuit breaker for wiring to the outlet is 8m. Furthermore, the outlet must not be dual-purpose. |  | Picture_10_A | Picture_10_B | Picture_10_C | Picture_10_D | 4 | ['兼用(けんよう)- Multi-use', '数値(すうち)- Numerical value', '分岐点(ぶんきてん)- Junction', '太い(ふと)- Fat; Thick', '分岐(ぶんき)- Divergence'] | {低圧}{屋内配線}の{分岐}{回路}の{設計}で、配線用{遮断器}、{分岐}{回路}の{電線}の太さ及び{コンセント}の{組合せ}として、{適切}なものは。 ただし、{分岐}点から配線用{遮断器}までは3m、配線用{遮断器}から{コンセント}までは8mとし、{電線}の{数値}は{分岐}{回路}の{電線}（軟{銅線}）の太さを{示す}。また、{コンセント}は{兼用}{コンセント}ではないものとする。 | Picture_10_A | Picture_10_B | Picture_10_C | Picture_10_D |  | 2020_1,
11 | What can be used when installing low-voltage underground wiring by direct burial? |  | 600V cross-linked polyethylene insulated vinyl sheath cable (CV) | Vinyl insulated wire for outdoor use (OW) | Vinyl insulated wire for lead-in (DV) | 600V vinyl insulated wire (IV) | 1 | ['使用(しよう)- Use', '直接(ちょくせつ)- Direct', '地中(ちちゅう)- Underground'] | {低圧}の{地中}{配線}を{直接}埋設式により{施設}する{場合}に{使用}できるものは。 | 600V{架橋}ポリエチレン{絶縁}ビニルシースケーブル（CV） | {屋外}用ビニル{絶縁}{電線}（OW） | 引込用ビニル{絶縁}{電線}（DV） | 600Vビニル{絶縁}{電線}（IV） |  | 2020_1,
12 | Judging from the allowable current, the most power-consuming electric heating appliance that can use a rubber cord has a nominal cross-sectional area of 1.25 mm2 (insulator is a mixture of natural rubber). However, the rated voltage of electric heating appliances shall be 100V and the ambient temperature shall be 30°C or less. |  | 600W electric rice cooker | 1000W toaster oven | 1500W electric water heater | 2000W electric dryer | 2 | ['定格(ていかく)- Rated value', '大きな(おおきな)- Big', '混合物(こんごうぶつ)- Mixture', '公称(こうしょう)- Public name', '判断(はんだん)- Judgment', '許容(きょよう)- Permission'] | {許容}{電流}から{判断}して、{公称}{断面積}1.25mm2のゴムコード（{絶縁}物が天然ゴムの{混合物}）を{使用}できる最も消費{電力}の{大きな}{電熱器}具は。 ただし、{電熱器}具の{定格}{電圧}は100Vで、{周囲}{温度}は30℃{以下}とする。 | 600Wの{電気}炊飯器 | 1000Wのオーブントースター | 1500Wの{電気}湯沸器 | 2000Wの{電気}乾燥器 |  | 2020_1,
| What is wrong as a combination of electrical work and tools to be used? |  | Drilling a hole in a metal cabinet and a knockout puncher | Drilling a hole in a wooden ceiling board for an electrical conduit and trimming a blade | Work to remove slack in electric wires, messenger wires, etc., and a wire tensione | Work to cut thin steel conduit and plica knife | 4 | ['木造り(きづく)- Wood construction', '電気工事(でんきこうじ)- Electrical work', '作業(さぎょう)- Work; operation'] | {電気}{工事}の{作業}と{使用}するエ具の{組合せ}として、誤っているものは。 | {金属}製キャビネットに穴をあける{作業}とノックアウトパンチャ | {木造}{天井}板に{電線}{管}を通す穴をあける{作業}と羽根ぎり | {電線}、メッセンジャワイヤ等のたるみを取る{作業}と張線器 | 薄鋼{電線}{管}を{切断}する{作業}とプリカナイフ |  | 2020_1,
14 | What is wrong in the description about the low-voltage three-phase squirrel cage induction motor for general use? |  | When the load increases, the rotational speed decreases slightly. | The starting current for full voltage starting (direct injection) is about 4 to 8 times the full load current. | Rotational speed increases when the frequency of the power supply changes from 60Hz to 50Hz. | Reversing any two of the three connections will reverse the rotation. | 3 | ['速度(そくど)- Velocity', '回転(かいてん)- Rotation', '記述(きじゅつ)- Description', '誘導電動機(ゆうどうでんどうき)- Induction motor'] | 一般用{低圧}{三相}かご形{誘導電動機}に関する{記述}で、誤っているものは。 | {負荷}が{増加}すると{回転}{速度}はやや低下する。 | 全{電圧}{始動}（じか入れ）での{始動}{電流}は全{負荷}{電流}の4~8倍{程度}である。 | {電源}の{周波数}が60Hzから50Hzに変わると{回転}{速度}が{増加}する。 | 3本の結{線}のうちいずれか2本を入れ替えると逆{回転}する。 |  | 2020_1,
15 | The limit of the time [minutes] that the circuit breaker must operate automatically when a current of 37.5 A continuously flows through a circuit breaker with a rated current of 30 A used in a low-voltage circuit (maximum time )teeth. |  | 2 | 4 | 60 | 120 | 3 | ['限度(げんど)- Limit', '継続(けいぞく)- Continuation', '電流(でんりゅう)- Electric current', '定格(ていかく)- Rated value'] | {低圧}{電路}に{使用}する{定格}{電流}30Aの{配線}用{遮断器}に37.5Aの{電流}が{継続}して流れたとき、この{配線}用{遮断器}が{自動}的に動作しなければならない時間［分］の{限度}（最大の時間）は。 | 2 | 4 | 60 | 120 |  | 2020_1,
16 | For the construction where the materials shown in the photo are used. |  | Metal duct work | Metal pipe work | Metal flexible conduit work | Metal wire work | 4 | ['材料(ざいりょう)- Materials; ingredients', '写真(しゃしん)- Photography'] | {写真}に{示す}{材料}が{使用}される{工事}は。 | {金属}ダクト{工事} | {金属}{管}{工事} | {金属}可とう{電線}{管}{工事} | {金属}{線}ぴ{工事} |  | 2020_1,
17 | What is the name of the part circled in the equipment shown in the photo? |  | Thermal Power Appliances | Earth leakage circuit breaker | Electromagnetic contactor | Leakage alarm | 3 | ['漏電(ろうでん)- Short circuit', '名称(めいしょう)- Name', '部分(ぶぶん)- Portion', '器具(きぐ)- Utensil'] | {写真}に{示す}{器具}の○で囲まれた{部分}の{名称}は。 | 熱動継電器 | {漏電}{遮断器} | {電磁}{接触}器 | {漏電}{警報器} |  | 2020_1,
18 | What is the purpose of the tool shown in the photo? | Picture_18 | Used for chamfering cut ends of metal pipes | Used for drilling iron plate | Used for drilling wooden poles. | Used for drilling holes in concrete walls | 2 | ['穴あけ(あな)- Drilling', '鉄板(てっぱん)- Iron plate', '面取り(めんと)- Chamfer', '工具(こうぐ)- Hand tool'] | {写真}に{示す}{工具}の{用途}は。 | {金属}{管}切り口の{面取り}に{使用}する。 | {鉄板}の{穴あけ}に{使用}する。 | 木柱の{穴あけ}に{使用}する。 | コンクリート{壁}の{穴あけ}に{使用}する。 |  | 2020_1,
19 | Indoor wiring with a working voltage of 100V is not suitable for construction work in humid locations. |  | Cable construction at the unfolded location | At the unfolded place, metal wire work | Metal pipe work with a moisture-proof device in a hidden place where inspection is not possible | Synthetic resin pipe work with a moisture-proof device in a concealed place that cannot be inspected (excluding CD pipes) | 2 | ['種類(しゅるい)- Variety', '場所(ばしょ)- Place', '湿気(しっけ)- Moisture', '電圧(でんあつ)- Voltage'] | {使用}{電圧}100Vの{屋内配線}で、{湿気}の多い{場所}における{工事}の{種類}として、{不適切}なものは。 | 展開した{場所}で、ケーブル{工事} | 展開した{場所}で、{金属}{線}ぴ{工事} | {点検}できない隠ぺい{場所}で、{防湿}装置を施した{金属}{管}{工事} | {点検}できない隠ぺい{場所}で、{防湿}装置を施した{合成}樹脂{管}{工事}（CD{管}を除く） |  | 2020_1,
20 | What are inappropriate construction methods for low-voltage indoor wiring? |  | In metal flexible conduit construction, stranded wires (insulated wires) were used to house the pipes without connecting parts. | In the lighting duct construction, the opening of the duct was installed facing downward. | In the metal wire work, the electric wire was branched within the 3 m long type 2 metal wire, and the D class grounding work was omitted. | In metal duct work, when branching electric wires, the connection part is covered with sufficient insulation and the connection part is housed in the duct so that it can be easily inspected. | 3 | ['点検(てんけん)- Nspection', '接続(せつぞく)- Connection ', '長さ(なが)- Length', 'より線(せん)- Stranded wire', '方法(ほうほう)- Method', '低圧(ていあつ)- Low voltage'] | {低圧}{屋内配線}の{工事}{方法}として、{不適切}なものは。 | {金属}可とう{電線}管{工事}で、{より線}（{絶縁}{電線}）を用いて、{管内}に{接続}{部分}を設けないで収めた。 | ライティングダクト{工事}で、ダクトの開口部を下に向けて{施設}した。 | {金属}線ぴ{工事}で、{長さ}3mの2{種}{金属}製線ぴ内で{電線}を{分岐}し、D{種}{接地}{工事}を{省略}した。 | {金属}ダクト{工事}で、{電線}を{分岐}する{場合}、{接続}{部分}に十分な{絶縁}{被覆}を施し、かつ、{接続}{部分}を{容易}に{点検}できるようにしてダクトに収めた。 |  | 2020_1,
21 | A three-phase 200V room air conditioner was installed indoors. What is the appropriate construction method? However, the ground voltage of the three-phase power supply shall be 200V, and the room air conditioner and wiring shall take simple contact protection measures. |  | A circuit breaker for wiring was attached to the electric circuit supplying the room air conditioner with a rated power consumption of 1.5 kW, wiring was made with synthetic resin pipes, and an outlet was used to connect to the room air conditioner. | A dedicated ground fault circuit breaker was attached to the electric circuit that supplies the room air conditioner with a rated power consumption of 1.5 kW, and wiring was made using synthetic resin pipes to connect directly to the room air conditioner. | A circuit breaker for wiring and an earth leakage circuit breaker were attached to the electric line that supplies the room air conditioner with a rated power consumption of 2.5 kW. | A circuit breaker for wiring was attached to the electric circuit that supplies the room air conditioner with a rated power consumption of 2.5 kW, wiring was made with metal pipes, and an outlet was used to connect the room air conditioner. | 3 | ['電路(でんろ)- Electrical circuit', '防護(ぼうご)- Protection', '電圧(でんあつ)- Voltage', '屋内(おくない)- Indoor', '住宅(じゅうたく)- Residence'] | {住宅}の{屋内}に{三相}200Vのルームエアコンを{施設}した。{工事}{方法}として、{適切}なものは。 ただし、{三相}{電源}の{対地}{電圧}は200Vで、ルームエアコン及び{配線}は{簡易}{接触}{防護}{措置}を施すものとする。 | {定格}消費{電力}が1.5kWのルームエアコンに供給する{電路}に、{専用}の{配線}用{遮断器}を取り付け、{合成}樹脂{管}{工事}で{配線}し、{コンセント}を{使用}してルームエアコンと{接続}した。 | {定格}消費{電力}が1.5kWのルームエアコンに供給する{電路}に、{専用}の{漏電}{遮断器}を取り付け、{合成}樹脂{管}{工事}で{配線}し、ルームエアコンと{直接}{接続}した。 | {定格}消費{電力}が2.5kWのルームエアコンに供給する{電路}に、{専用}の{配線}用{遮断器}と{漏電}{遮断器}を取り付け、ケーブル{工事}で{配線}し、ルームエアコンと{直接}{接続}した。 | {定格}消費{電力}が2.5kWのルームエアコンに供給する{電路}に、{専用}の{配線}用{遮断器}を取り付け、{金属}{管}{工事}で{配線}し、{コンセント}を{使用}してルームエアコンと{接続}した。 |  | 2020_1,
22 | For low-voltage indoor wiring work installed in a dry place with simple contact protection measures, D-class grounding work cannot be omitted. |  | Metal box used for 3-phase 3-wire 200V synthetic resin pipe work | Three-phase three-wire 200V metal pipe construction with a total length of 5 m | Single-phase 100V electric motor platform | A metal pipe with a total length of 5m containing electric wires in single-phase 100V metal pipe construction | 2 | ['金属製(きんぞくせい)- Made of metal', '省略(しょうりゃく)- Omission; abbreviation', '接触(せっしょく)- Touch', '簡易(かんい)- Simplicity'] | {簡易}{接触}{防護}{措置}を施した乾燥した{場所}に{施設}する{低圧}{屋内配線}{工事}で、D{種}{接地}{工事}を{省略}できないものは。 | {三相}3{線}式200Vの{合成}樹脂{管}{工事}に{使用}する{金属}製ボックス | {三相}3線式200Vの{金属}{管}{工事}で{電線}を収める{管}の全長が5mの{金属}{管} | {単相}100Vの{電動機}の鉄台 | {単相}100Vの{金属}{管}{工事}で{電線}を収める{管}の全長が5mの{金属}{管} |  | 2020_1,
23 | What is inappropriate as a synthetic resin pipe construction using hard vinyl chloride conduit? |  | The distance between pipe support points is 2m | A dedicated adhesive was used to connect the tubes to each other and to the box, and the insertion depth of the tubes was 0.9 times the outer diameter of the tubes. | A moisture-proof device was applied to the connection point between the pipe and the box installed in a humid place. | D-class grounding work was performed on a metal pull box connected to a pipe installed in a place where simple contact protection measures were taken with three-phase 200V wiring. | 1 | ['管(かん)- Pipe; Tube', '箇所(かしょ)- Place; point', '接続(せつぞく)- Connection', '距離(きょり)- Distance'] | {硬質}塩化ビニル{電線}{管}による{合成}樹脂{管}{工事}として、{不適切}なものは。 | {管}の支持点間の{距離}は2mとした。 | {管}{相互}及び{管}とボックスとの{接続}で、{専用}の接着剤を{使用}し、{管}の差込み深さを{管}の{外径}の0.9倍とした。 | {湿気}の多い{場所}に{施設}した{管}とボックスとの{接続}{箇所}に、{防湿}装置を施した。 | {三相}200V{配線}で、{簡易}{接触}{防護}{措置}を施した{場所}に{施設}した{管}と{接続}する{金属}製プルボックスに、D{種}{接地}{工事}を施した。 |  | 2020_1,
24 | In a single-phase three-wire system 100/200V indoor wiring using three kinds of electric wires with red, white, and black insulation colors, the voltages between the wires and between the wires and the ground were measured. As a result, which voltage combination is suitable? However, the neutral wire should be white. |  | Between red line and ground: 200V Between white line and ground: 100V Between black line and ground: 0V | Between red line and black line: 100V Between red line and ground: 0V Between black line and ground: 200V | Between red line and white line: 200V between red line and ground: 0V、 between black line and ground: 100V | Between red line and black line: 200 V Between white line and ground: 0 V Between black line and ground: 100 V | 4 | ['種類(しゅるい)- Variety; kind; type', '赤色(あかいろ)- Red color', '被覆(ひふく)- Cover'] | {絶縁}{被覆}の色が{赤色}、白色、黒色の3{種類}の{電線}を{使用}した{単相}3線式100/200V{屋内配線}で、{電線}{相互}間及び{電線}と{大地}間の{電圧}を{測定}した。その{結果}として、{電圧}の{組合せ}で、{適切}なものは。 ただし、中性線は白色とする。 | {赤色}{線}と{大地}間 ：200V 白色{線}と{大地}間：100V 黒色{線}と{大地}間：0V | {赤色}{線}と黒色{線}間：100V {赤色}{線}と{大地}間：0V 黒色{線}と{大地}間：200V | {赤色}{線}と白色{線}間：200V {赤色}{線}と{大地}間：0V 黒色{線}と{大地}間：100V | {赤色}{線}と黒色{線}間：200V 白色{線}と{大地}間：0V 黒色{線}と{大地}間：100V |  | 2020_1,
25 | We measured the insulation resistance between the electric circuit of the low-voltage indoor wiring and the ground. Those that do not conform to the "Ministerial Ordinance for Establishing Technical Standards for Electrical Equipment". |  | The insulation resistance of a single-phase three-wire 100/200V air conditioning circuit with a working voltage of 200V was measured and found to be 0.16MΩ. | The insulation resistance of the 3-phase 3-wire motor circuit with a working voltage of 200 V (voltage to ground: 200 V) was 0.18 MΩ. | The insulation resistance of a single-phase two-wire outdoor garden lighting circuit with a working voltage of 100 V was 0.12 MΩ. | The insulation resistance of the single-phase two-wire indoor wiring with a working voltage of 100 V was measured on the distribution board for each circuit at once, and it was 1.5 MΩ, so measurement of individual branch circuits was omitted. | 2 | ['電動機(でんどうき)- Electric motor', '対地(たいち)- Ground to ground', '省令(しょうれい)-ministerial ordinance', '技術基準(ぎじゅつきじゅん)-Technical standards', '屋内配線(おくないはいせん) - Interior wiring'] | {低圧}{屋内配線}の{電路}と{大地}間の{絶縁}抵抗を{測定}した。「{電気}{設備}に関する{技術基準}を定める{省令}」に適合していないものは。 | {単相}3{線}式100/200Vの{使用}{電圧}200V空調{回路}の{絶縁}抵抗を{測定}したところ0.16MΩであった。 | {三相}3{線}式の{使用}{電圧}200V（{対地}{電圧}200V）{電動機}{回路}の{絶縁}抵抗を{測定}したところ0.18MΩであった。 | {単相}2{線}式の{使用}{電圧}100V{屋外}庭園灯{回路}の{絶縁}抵抗を{測定}したところ0.12MΩであった。 | {単相}2線式の{使用}{電圧}100V{屋内配線}の{絶縁}抵抗を、{分電盤}で各{回路}を一括して{測定}したところ、1.5MΩであったので個別{分岐}{回路}の{測定}を{省略}した。 |  | 2020_1,
26 | We measured the grounding resistance value of the groundwork installed on the steel base of the three-phase 200V three-phase induction motor in the factory and inspected the thickness of the grounding wire (annealed copper wire). What is an appropriate combination of grounding resistance value [Ω] and grounding wire thickness (diameter [mm]) that conforms to the "Interpretation of Technical Standards for Electrical Equipment"? The operation time of an earth leakage circuit breaker installed in an electric circuit, on the other hand, must be 0.1 second. |  | Ground resistance value: 100Ω Ground wire diameter: 1.0mm | Ground resistance value: 200Ω Ground wire diameter: 1.2mm | Ground resistance value: 300Ω Ground wire diameter: 1.6mm | Ground resistance value: 600Ω Ground Line diameter: 2.0m | 2 | ['直径(ちょっけい)- Diameter', '動作時間(どうさじかん)- Operating time', '電路(でんろ)- Electrical circuit', '工場(こうじょう)- Factory'] | {工場}の{三相}200V{三相}{誘導電動機}の鉄台に{施設}した{接地}{工事}の{接地}抵抗{値}を{測定}し、{接地}線（軟{銅線}）の太さを{検査}した。「{電気}{設備}の{技術基準}の{解釈}」に適合する{接地}抵抗{値}［Ω］と{接地}線の太さ（{直径}［mm］）の{組合せ}で、{適切}なものは。 ただし、{電路}に{施設}された{漏電}{遮断器}の{動作時間}は、0.1秒とする。 | {接地}抵抗{値}：100Ω {接地}{線}の{直径}：1.0mm | {接地}抵抗{値}：200Ω {接地}{線}の{直径}：1.2mm | {接地}抵抗{値}：300Ω {接地}{線}の{直径}：1.6mm | {接地}抵抗{値}：600Ω {接地}{線}の{直径}：2.0mm |  | 2020_1,
27 | There is a symbol as shown in the figure on the scale plate of the direct-acting indicating electric meter. What is the correct meaning of the symbols and which circuits can be measured? | Picture_27 | It is a permanent magnet moving coil type with a scale plate placed horizontally and used in a DC circuit. | It is a permanent magnet moving coil type with a scale plate placed horizontally and used in an AC circuit. | It is a movable iron type with a vertical dial and used in a DC circuit. | It is a movable iron type with a scale plate placed horizontally and used in an AC circuit. | 1 | ['水平(すいへい)- Horizontal plane', '問題(もんだい)- Problem', '指示(しじ)- Instructions'] | 直動式{指示}{電気}{計器}の目盛板に{図}のような{記号}がある。{記号}の意味及び{測定}できる{回路}で、{正しい}ものは。 | 永久磁石{可動}{コイル}形で目盛板を{水平}に置いて、{直流}{回路}で{使用}する。 | 永久磁石{可動}{コイル}形で目盛板を{水平}に置いて、{交流}{回路}で{使用}する。 | {可動}鉄片形で目盛板を鉛直に立てて、{直流}{回路}で{使用}する。 | {可動}鉄片形で目盛板を{水平}に置いて、{交流}{回路}で{使用}する。 |  | 2020_1,
28 | What is the main purpose of the Electrician Law? |  | Establishes the qualifications of chief electricians engaged in electrical work. | Clarify the duty of safety inspection of electric facilities. | Identify the identity of an electrician. | Contributes to the prevention of disasters caused by defects in electrical work. | 4 | ['義務(ぎむ)- Duty', '主任(しゅにん)- Person in charge', '電気工事(でんきこうじ)- Electrical work', '目的(もくてき)- Purpose; goal'] | 「{電気}{工事}士法」の主な{目的}は。 | {電気}{工事}に{従事}する{主任}{電気}{工事}士の{資格}を定める。 | {電気}工{作物}の{保安}調査の{義務}を明らかにする。 | {電気}{工事}士の身分を明らかにする。 | {電気}{工事}の欠陥による災害{発生}の防止に寄与する。 |  | 2020_1,
29 | Which of the following is the correct combination of specific electrical appliances to be used in low-voltage indoor electric circuits? A. Leakage circuit breaker with rated voltage of 100V and rated current of 20A B. Replacing fan with fixed voltage of 100V and fixed consumption of 25W C. 3-core vinyl-insulated vinyl-sheathed cable with a rated voltage of 600 V and a conductor thickness (diameter) of 2.0 mm D. Synthetic resin flexible conduit (PF tube) with an inner diameter of 16 mm |  | A and B | A and C | B and D | C and D | 2 | ['導体(どうたい)- Conductor (electricity)', '絶縁(ぜつえん)- Insulation', '定格(ていかく)- Rated value', '用品(ようひん)- Articles', '屋内(おくない)- Indoor', '低圧(ていあつ)- Low voltage'] | {低圧}の{屋内}{電路}に{使用}する次のもののうち、{特定}{電気}{用品}の{組合せ}として、{正しい}ものは。 A：{定格}{電圧}100V、{定格}{電流}20Aの{漏電}{遮断器} B：{定格}{電圧}100V、{定格}消費{電力}25Wの換気扇 C：{定格}{電圧}600V、{導体}の太さ（{直径}）2.0mmの3心ビニル{絶縁}ビニルシースケーブル D：{内径}16mmの{合成}樹脂製可とう{電線}{管}（PF{管}） | A and B | A and C | B and D | C and D |  | 2020_1,
30 | What is the correct statement regarding general electric equipment? The voltage of the power generation equipment, however, must be 600 volts or less. |  | Those that receive power at low voltage are treated as electric facilities for general use, even if a 55 kW output solar cell power generation facility is installed on the same premises. | Those that receive power at low voltage are considered to be electric facilities for general use even if a small output power generation facility is installed in the same premises. | Even if it receives power at a high voltage, it may become a general-use electric facility depending on the type of business where it is demanded. | Anything that receives power at high voltage is a general-purpose electric facility, regardless of the capacity of the power received or the type of industry in which it is demanded. | 2 | ['発電(はつでん)- Electricity generation', '出力(しゅつりょく)- Output', '設備(せつび) - Equipment', '記述(きじゅつ)- Dscription; account'] | 一般用{電気}工{作物}に関する{記述}として、{正しい}ものは。 ただし、{発電}{設備}は{電圧}600V{以下}とする。 | {低圧}で{受電}するものは、{出力}55kWの太陽{電池}{発電}{設備}を同一{構内}に{施設}しても、一般用{電気}工{作物}となる。 | {低圧}で{受電}するものは、小{出力}{発電}{設備}を同一{構内}に{施設}しても、一般用{電気}工{作物}となる。 | {高圧}で{受電}するものであっても、{需要}{場所}の業{種}によっては、一般用{電気}工{作物}になる{場合}がある。 | {高圧}で{受電}するものは、{受電}{電力}の{容量}、{需要}{場所}の業{種}にかかわらず、すべて一般用{電気}工{作物}となる。 |  | 2020_1,
31 | What is the type of instrument for the symbol shown in (1) ? |  | Ceiling (directly attached to the ceiling) | Pendant | Embedded fixture | Hanging ceiling (round) | 1 | ['器具(きぐ)- Tool; instrument', '記号(きごう)-Symbol; code'] | ①で{示す}{図}{記号}の{器具}の{種類}は。 | シーリング（{天井}直付） | ペンダント | 埋込{器具} | 引掛シーリング（丸） |  | 2020_1,
32 | What is the minimum number of wires (number of cores) for the part indicated by ②? |  | 2 | 3 | 4 | 5 | 2 | ['最少(さいしょう)- Fewest', '部分(ぶぶん)- Portion'] | ②で{示す}{部分}の{最少}{電線}{本数}（心線数）は。 | 2 | 3 | 4 | 5 |  | 2020_1,
33 | What is the minimum conductor diameter [mm] of the electric wire (annealed copper wire) that can be used in the small force circuit shown in ③? |  | 0.5 | 0.8 | 1.2 | 1.6 | 2 | ['道(みち)- Road; path', '電線(でんせん)- Cable', '回路(かいろ)- Circuit'] | ③で{示す}{部分}の小{勢力}{回路}で{使用}できる{電線}（軟{銅線}）の{導体}の{最小}{直径}［mm］は。 | 0.5 | 0.8 | 1.2 | 1.6 |  | 2020_1,
34 | The part indicated by ④ is the outdoor unit of the room air conditioner. The sidenote indication of the graphic symbol is. |  | O | B | I | R | 1 | ['部分(ぶぶん)- Portion', '表示(ひょうじ)- Indication'] | ④で{示す}{部分}はルームエアコンの{屋外}ユニットである。その{図}{記号}の傍記{表示}は。 | O | B | I | R |  | 2020_1,
35 | What is the minimum allowable insulation resistance [MΩ] between the electric circuit and the ground in the part indicated by ⑤? |  | 0.1 | 0.2 | 0.4 | 1 | 1 | ['最小値(さいしょうち)- Minimum value;', '絶縁抵抗(ぜつえんていこう)- Insulation resistance', '電路(でんろ)- Electrical circuit'] | ⑤で{示す}{部分}の{電路}と{大地}間の{絶縁}抵抗として、{許容}される{最小}{値}［MΩ］は。 | 0.1 | 0.2 | 0.4 | 1 |  | 2020_1,
36 | What is the correct combination of the type of grounding work for the part shown in ⑥ and the maximum allowable value [Ω] of the grounding resistance? |  | C-class grounding work Maximum allowable ground resistance: 10Ω | C-type grounding work Maximum allowable grounding resistance: 50Ω | D-type grounding work Maximum allowable grounding resistance: 100Ω | Class D grounding work Maximum allowable grounding resistance: 500Ω | 4 | ['接地(せっち)- Ground (electricity)', '抵抗(ていこう)- Resistance', '種類(しゅるい)- Variety; kind'] | ⑥で{示す}{部分}の{接地}{工事}の{種類}及びその{接地}抵抗の{許容}される{最大値}［Ω］の{組合せ}として、{正しい}ものは。 | C{種}{接地}{工事} {許容}される{接地}抵抗の{最大値}：10Ω | C{種}{接地}{工事} {許容}される{接地}抵抗の{最大値}：50Ω | D{種}{接地}{工事} {許容}される{接地}抵抗の{最大値}：100Ω | D{種}{接地}{工事} {許容}される{接地}抵抗の{最大値}：500Ω |  | 2020_1,
37 | What can be used for the part indicated by ⑦? |  | Rubber insulated round cord | Vinyl insulated lead wire | Crosslinked polyethylene insulated vinyl sheath cable | Vinyl insulated wire for outdoor use | 3 | ['架橋(かきょう)- Cross-link', '画像(がぞう)- Image', '問題(もんだい)- Question'] | ⑦で{示す}{部分}に{使用}できるものは。 | ゴム{絶縁}丸打コード | 引込用ビニル{絶縁}{電線} | {架橋}ポリエチレン{絶縁}ビニルシースケーブル | {屋外}用ビニル{絶縁}{電線} |  | 2020_1,
38 | What is the maximum length [m] of the electric circuit between the house and the garage when the service entrance switch shown in ⑧ can be omitted? |  | 8 | 10 | 15 | 20 | 3 | ['最大値(-さいだいち)-Greatest value', '電路(でんろ)- Electrical circuit', '住宅(じゅうたく)- Residence', '場合(ばあい)- Case; situation'] | ⑧で{示す}引込口{開閉器}が{省略}できる{場合}の、{住宅}と車庫との間の{電路}の{長さ}の{最大値}［m］は。 | 8 | 10 | 15 | 20 |  | 2020_1,
39 | What kind of pipe is used for the wiring work of the part indicated by ⑨? |  | Shock-resistant hardened plastic wire tube | Corrugated rigid synthetic resin tube | Rigid chemical plastic wire tube | Synthetic resin-made plastic wire tube | 4 | ['硬質(こうしつ)- Hardness', '種類(しゅるい)- Variety; kind'] | ⑨で{示す}{部分}の{配線}{工事}で用いる{管}の{種類}は。 | 耐衝撃性{硬質}塩化ビニル{電線}{管} | 波付{硬質}{合成}樹脂{管} | {硬質}塩化ビニル{電線}{管} | {合成}樹脂製可とう{電線}{管} |  | 2020_1,
40 | What is the correct construction method for the part indicated by ⑩? |  | Metal wire work | Cable work (VVR) | Metal duct work | Metal pipe work | 2 | ['画像(がぞう)- Image', '工事(こうじ)- Construction work'] | ⑩で{示す}{部分}の{工事}{方法}として、{正しい}ものは。 | {金属}{線}ぴ{工事} | ケーブル{工事}（VVR） | {金属}ダクト{工事} | {金属}{管}{工事} |  | 2020_1,
41 | What cables are necessary for the wiring work of the part indicated by ⑪? However, the number of core wires should be the minimum. |  | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D | 2 | ['最少(さいしょう)- Fewest', '配線工事(はいせんこうじ)- Wiring work'] | ⑪で{示す}{部分}の{配線}{工事}に{必要}なケーブルは。 ただし、心線数は{最少}とする。 | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D |  | 2020_1,
42 | When the connection in the box shown in ⑫ is crimped with a ring sleeve, what is the correct combination of the ring sleeve type, number, and stamp after the crimped connection? However, the wire to be used should be VVF1.6 unless otherwise specified. In addition, ○, small, and medium in the center of the ring sleeve shown in the photograph represent engravings. |  | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D | 4 | ['個数(こすう)- Number of articles', '種類(しゅるい)- Variety; kind', '圧着(あっちゃく)- Crimping', '接続(せつぞく)- Connection'] | ⑫で{示す}ボックス内の{接続}をリングスリーブで{圧着}{接続}した{場合}のリングスリーブの{種類}、{個数}及び{圧着}{接続}後の{刻印}との{組合せ}で、{正しい}ものは。 ただし、{使用}する{電線}は{特記}のないものはVVF1.6とする。また、{写真}に{示す}リングスリーブ{中央}の○、小、中は{刻印}を表す。 | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D |  | 2020_1,
43 | If all the connections in the box indicated by ⑬ are plug-in connectors, what is the correct combination of the type of plug-in connectors to be used and the minimum number? However, the wire to be used should be VVF1.6. |  | Picture_43_A | Picture_43_B | Picture_42_C | Picture_43_D | 1 | ['種類(-しゅるい)- Kind; type', '場合(ばあい)- Case', '接続(せつぞく)- Connection'] | ⑬で{示す}ボックス内の{接続}をすべて差込形{コネクタ}とする{場合}、{使用}する差込形{コネクタ}の{種類}と{最少}{個数}の{組合せ}で、{正しい}ものは。ただし、{使用}する{電線}はVVF1.6とする。 | Picture_43_A | Picture_43_B | Picture_42_C | Picture_43_D |  | 2020_1,
44 | ⑭ What is the equipment with the symbol shown in ⑭? However, the diagram below the photo shows the configuration of the contacts |  | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D | 3 | ['構成(こうせい)- Composition', '接点(せってん)- Tangent point', '記号(きごう)- Symbol'] | ⑭で{示す}{図}{記号}の{器具}は。ただし、{写真}下の{図}は、{接点}の{構成}を{示す}。 | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D |  | 2020_1,
45 | ⑮ The equipment with the symbol shown in |  | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D | 1 | ['器具(きぐ)- Tool; Instrument'] | ⑮で{示す}{図}{記号}の{器具}は。 | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D |  | 2020_1,
46 | Equipment to be attached to the part indicated by ⑯. |  | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D | 3 | ['機器(きき)- Device'] | ⑯で{示す}{部分}に取り付ける{機器}は。 | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D |  | 2020_1,
47 | What are the tools that are not generally used for the wiring work of the part indicated by ⑰? |  | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D | 4 | ['配線工事(はいせんこうじ)- Wiring work;'] | ⑰で{示す}{部分}の{配線}{工事}で、{一般的}に{使用}されることのない{工具}は。 | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D |  | 2020_1,
48 | If all the connections in the box shown in ⑱ are crimp connections, what is the correct combination of ring sleeve type and minimum number to be used? However, the wire to be used should be VVF1.6 unless otherwise specified. |  | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D | 1 | ['特記(とっき)- Special mention', '種類(しゅるい)- Variety', '圧着(あっちゃく)- Crimping', '接続(せつぞく)- Connection'] | ⑱で{示す}ボックス内の{接続}をすべて{圧着}{接続}とする{場合}、{使用}するリングスリーブの{種類}と{最少}{個数}の{組合せ}で、{正しい}ものは。 ただし、{使用}する{電線}は{特記}のないものはVVF1.6とする。 | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D |  | 2020_1,
49 | An unused outlet is a symbol in this wiring diagram. |  | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D | 4 | ['配線図(はいせんず)- Wiring diagram'] | この{配線}{図}の{図}{記号}で、{使用}されていない{コンセント}は。 | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D |  | 2020_1,
50 | Regarding the construction of this wiring diagram, what is the wrong combination of items to be used? |  | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D | 2 | ['に関して(かん)- Related to', '施工(せこう)- Construction'] | この{配線}{図}の{施工}{に関して}、{使用}するものの{組合せ}で、誤っているものは。 | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D |  | 2020_1,