## Sheet1
no | Eng | Picture | Option_1_Eng | Option_2_Eng | Option_3_Eng | Option_4_Eng | Ans | Vocab | Jpn | Option_1_Jpn | Option_2_Jpn | Option_3_Jpn | Option_4_Jpn | Exp | comment
1 | In the DC circuit as shown in the figure, the voltage [V] between a and b is. | Picture_1 | 10 | 20 | 30 | 40 | 2 | ['電圧(でんあつ)- Voltage'] | {図}のような{直流}{回路}で、a−b間の{電圧}［V］は。 | 10 | 20 | 30 | 40 | Voltage is 100+100=200V. Circuit is I=E/R=200/50=4A. Voltage is E=IR=4×20=80V Power supply is 100V, 100-80=20V | 2020_2,
2 | There are two copper wires of the same material, A and B. A is 1.6mm in diameter and 100m in length, B is 3.2mm in diameter and 50m in length. How many times is the resistance of A greater than the resistance of B? |  | 2 | 4 | 4 | 8 | 4 | ['長さ(なが)- Length', '直径(ちょっけい)- Diameter', '材質(ざいしつ)- Material'] | A、B2本の同{材質}の{銅線}がある。Aは{直径}1.6mm、{長さ}100m、Bは{直径}3.2mm、{長さ}50mである。Aの抵抗はBの抵抗の何倍か。 | 2 | 4 | 4 | 8 |  | 2020_2,
3 | The contact resistance at the connection point became 0.2Ω due to poor connection of the electric wire. If a current of 10A flows through this wire, what is the amount of heat [kJ] generated in one hour from the connection point? However, it is assumed that the value of the contact resistance does not change. |  | 72 | 144 | 288 | 576 | 1 | ['電流(でんりゅう)- Electric current', '抵抗(ていこう)- Resistance', '接触(せっしょく)- Touch', '不良(ふりょう)- Bad; Poor', '接続(せつぞく)- Connection', '電線(でんせん)- Electric cable'] | {電線}の{接続}{不良}により、{接続}点の{接触}抵抗が0.2Ωとなった。この{電線}に10Aの{電流}が{流れる}と、{接続}点から1時間に{発生}する{熱量}［kJ］は。 ただし、{接触}抵抗の{値}は変化しないものとする。 | 72 | 144 | 288 | 576 | H=10*10*0.2*3600 =72000（J） =72（kJ) | 2020_2,
4 | In the AC circuit shown in the figure, when the power supply voltage is 204 V, the voltage across the resistor is 180 V, and the voltage across the reactance is 96 V, the power factor [%] of the load is: | Picture_4 | 35 | 47 | 65 | 88 | 4 | ['熱量(ねつりょう)- Quantity of heat '] | {図}のような{交流}{回路}で、{電源}{電圧}204V、抵抗の{両端}の{電圧}が180V、リアクタンスの{両端}の{電圧}が96Vであるとき、{負荷}の{力率}［%］は。 | 35 | 47 | 65 | 88 | Cosθ ＝ Vr/V ＝180/204 ＝0.8823… ≒ 0.88 Percentage of 100, it will be 88%. | 2020_2,
5 | When a three-phase AC voltage was applied to the three-phase load shown in the figure, a current of 15A flowed through each line. Line voltage E [V] is | Picture_5 | 150 | 212 | 260 | 300 | 3 | ['流れる(なが)- To stream; To flow', '負荷(ふか)- Load', '三相(さんそう)- Three phases'] | {図}のような{三相}{負荷}に{三相}{交流}{電圧}を加えたとき、各{線}に15Aの{電流}が流れた。{線}間{電圧}E［V］は。 | 150 | 212 | 260 | 300 | V = IR = 15×10 = 150V E = √3V So, E = 1.73×150 = 259.5 ≒260 | 2020_2,
6 | As shown in the figure, the voltage across the load was 100V when power was supplied to a resistance load with a power consumption of 1600W through a wire length of 12m. What is the voltage drop [V] in the wiring? The electrical resistance of the wire, however, must be 5.0 per 1000m of length. | Picture_6 | 1 | 2 | 3 | 4 | 2 | ['電圧降下(でんあつこうか)- Voltage drop', '結果(けっか)- Result', '配線(はいせん)- Wiring'] | {図}のように、{電線}のこう長12mの{配線}により、消費{電力}1600Wの抵抗{負荷}に{電力}を供給した{結果}、{負荷}の{両端}の{電圧}は100Vであった。{配線}における{電圧}降下［V］は。 ただし、{電線}の{電気}抵抗は{長さ}1000m{当たり}5.0Ωとする。 | 1 | 2 | 3 | 4 | The wire length is 12+12 or 24 (m). From the title, it is 5Ω per 1000m length, so it is 0.005Ω per 1m, and it can be calculated as 0.12Ω resistance at 24m. V=IR, V=16*0.12 = 1.92 ≒ 2 | 2020_2,
7 | In a single-phase three-wire circuit as shown in the figure, when the resistance of each wire is 0.1Ω and the current flowing through the resistive load is 20A, the power loss [W] of this wire line is: |  | 40 | 69 | 80 | 120 | 3 | ['電流(でんりゅう)- Electric current', '回路(かいろ)- Circuit'] | {図}のような{単相}3線式{回路}で、{電線}1線{当たり}の抵抗が0.1Ω、抵抗{負荷}に{流れる}{電流}がともに20Aのとき、この{電線}路の{電力}損失［W］は。 | 40 | 69 | 80 | 120 | Substitute 0.1Ω for resistance and 20A for current here. P = 2 x 0.1 x 20 x 20 = 80 [W] | 2020_2,
8 | When installing four 600V vinyl insulated wires (annealed copper wires) with a cross-sectional area of ​​3.5 mm2 in a low-voltage indoor wiring work using metal pipes, what is the allowable current [A] per wire? However, the ambient temperature should be 30°C or less, and the current reduction factor should be 0.63. |  | 19 | 23 | 31 | 49 | 2 | ['係数(けいすう)- Coefficient', '許容(きょよう)- Permission', '電線(でんせん)- Cable', '絶縁(ぜつえん)- Insulation ', '低圧(ていあつ)- Low Voltage'] | {金属}管による{低圧}{屋内配線}{工事}で、{管内}に{断面積}3.5mm2の600Vビニル{絶縁}{電線}（軟{銅線}）4本を収めて{施設}した{場合}、{電線}1本{当たり}の{許容}{電流}［A］は。 ただし、{周囲}{温度}は30℃{以下}、{電流}{減少}{係数}は0.63とする。 | 19 | 23 | 31 | 49 | allowable current is 37×0.63=23.31[A] | 2020_2,
9 | There is a single-phase two-wire low-voltage indoor trunk line connected to five motors with a rated current of 12A. What is the minimum value of current [A] that is the basis for determining the thickness of this main line? However, the demand rate is assumed to be 80%. |  | 48 | 60 | 66 | 75 | 2 | ['幹線(かんせん)- Main line', '単相(たんそう)- Single phase', '根拠(こんきょ)- Grounds', '定格(ていかく)- Rated value'] | {定格}{電流}12Aの{電動機}5台が{接続}された{単相}2線式の{低圧}{屋内}{幹線}がある。この{幹線}の太さを決定するための{根拠}となる{電流}の{最小}{値}［A］は。 ただし、{需要}率は80%とする。 | 48 | 60 | 66 | 75 | The rated current is calculated as 5×12×0.8 = 48(A). The allowable current of the main line is 48 x 1.25 = 60 (A) because there is a rule that if the total rated current of the motor, etc. is 50A or less, it should be 1.25 times the rated current. | 2020_2,
10 | In the design of branch circuits for low-voltage indoor wiring, what is the appropriate combination of circuit breakers, branch circuit wire thicknesses, and outlets? However, the distance from the branch point to the circuit breaker for wiring is 3 m, and the distance from the circuit breaker for wiring to the outlet is 8 m. Furthermore, the outlet must not be dual-purpose. |  | Picture_10_A | Picture_10_B | Picture_10_C | Picture_10_D | 3 | ['容易(ようい)- Easy', '多数(たすう)- Large number'] | {低圧}{屋内配線}の{分岐}{回路}の{設計}で、配線用{遮断器}、{分岐}{回路}の{電線}の太さ及び{コンセント}の{組合せ}として、{適切}なものは。 ただし、{分岐}点から配線用{遮断器}までは3m、配線用{遮断器}から{コンセント}までは8mとし、{電線}の{数値}は{分岐}{回路}の{電線}（軟{銅線}）の太さを{示す}。 また{コンセント}は{兼用}{コンセント}ではないものとする。 | Picture_10_A | Picture_10_B | Picture_10_C | Picture_10_D |  | 2020_2,
11 | Used to facilitate wiring in places where many metal pipes are gathered. |  | Distribution board | Pull box | Fixture stud | Switch box | 2 |  | {多数}の{金属}{管}が{集合}する{場所}等で、通{線}を{容易}にするために用いられるものは。 | {分電盤} | プルボックス | フィクスチュアスタッド | {スイッチ}ボックス |  | 2020_2,
12 | Which insulator has the highest maximum permissible temperature? |  | 600V cross-linked polyethylene insulated vinyl sheath cable (CV) | 600V class 2 vinyl insulated wire (HIV) | 600V Vinyl Insulated Vinyl Sheath Cable Round (VVR) | 600V vinyl insulated wire (IV) | 1 | ['高い(たか)- High', '温度(おんど)- Temperature', '物の(もの)- Only', '絶縁(ぜつえん)- Insulation '] | {絶縁}{物の}最高{許容}{温度}が最も{高い}ものは。 | 600V{架橋}ポリエチレン{絶縁}ビニルシースケーブル（CV） | 600V二{種}ビニル{絶縁}{電線}（HIV） | 600Vビニル{絶縁}ビニルシースケーブル丸形（VVR） | 600Vビニル{絶縁}{電線}（IV） |  | 2020_2,
13 | What tools are used for bending threadless conduits? |  | Torch lamp | Disc grinder | Pipe wrench | Pipe bender | 4 | ['電線(でんせん)- Cable'] | ねじなし{電線}{管}の曲げ加工に{使用}するエ具は。 | トーチランプ | ディスクグラインダ | パイプレンチ | パイプベンダ |  | 2020_2,
14 | What is the synchronous speed [min-1] of a low-voltage three-phase squirrel-cage induction motor with a rated frequency of 60 Hz and four poles? |  | 1200 | 1500 | 1800 | 3000 | 3 | ['同期(どうき)- Synchronization', '低圧(ていあつ)- Low voltage', '極(きょく)- Pole', '周波数(しゅうはすう)-Frequency'] | {定格}{周波数}60Hz、{極}数4の{低圧}{三相}かご形{誘導電動機}の{同期}{速度}［min−1］は。 | 1200 | 1500 | 1800 | 3000 |  | 2020_2,
15 | What is the role of the zero-phase current transformer built into the earth leakage breaker? |  | Undervoltage detection | Short-circuit current detection | Overvoltage detection | Ground fault current detection | 4 | ['不足(ふそく)- Insufficiency', '役割(やくわり)- Role', '変流器(へんりゅうき)- Transformer'] | {漏電}{遮断器}に内蔵されている零相{変流器}の{役割}は。 1 .{不足}{電圧}の{検出} 2 .短絡{電流}の{検出} 3 .過{電圧}の{検出} 4 .地絡{電流}の{検出} | Undervoltage detection | Short-circuit current detection | Overvoltage detection | Ground fault current detection |  | 2020_2,
16 | What is the name of the material shown in the photo? | Picture_16 | Universal | Normal bend | Bender | Coupling | 2 | ['材料(ざいりょう)-Materials', '写真(しゃしん)-Photography'] | {写真}に{示す}{材料}の{名称}は。 | ユニバーサル | ノーマルベンド | ベンダ | カップリング |  | 2020_2,
| What is the purpose of the equipment shown in the photo? | Picture_17 | Improve the power factor of the circuit. | Detect ground fault current. | Turn on the neon discharge lamp. | Stabilize the discharge of mercury lamps | 1 | ['力率(りきりつ)- Power factor', '機器(きき)- Equipment'] | {写真}に{示す}{機器}の{用途}は。 | {回路}の{力率}を改善する。 | 地絡{電流}を{検出}する。 | ネオン放{電灯}を{点灯}させる。 | {水銀灯}の放電を安定させる。 |  | 2020_2,
18 | What is the name of the measuring instrument shown in the photo? |  | Frequency meter | Phase detector | Illuminance meter | Clamp ammeter | 3 | ['電流計(でんりゅうけい)- Ammeter', '測定器(そくていき)- Measuring instrument'] | {写真}に{示す}{測定}器の{名称}は。 | {周波数}計 | 検相器 | {照度}計 | クランプ形{電流}計 |  | 2020_2,
19 | In low-voltage indoor wiring work using 600V vinyl-insulated vinyl-sheathed flat cables of 1.6 mm, what is inappropriate as insulation treatment for the terminal connection part between insulation wires? However, the vinyl tape must be a JIS-specified polyvinyl chloride adhesive tape for electrical insulation with a thickness of about 0.2 mm. |  | They were connected by a ring sleeve (E type), and the connecting part was wrapped once (two layers) with a self-adhesive insulating tape (thickness of about 0.5 mm) overlapping more than half the width. | They were connected by a ring sleeve (E type), and a black adhesive polyethylene insulating tape (thickness: about 0.5 mm) was wrapped three times (6 layers) around half width or more. | Connected with a ring sleeve (E type) and wrapped with vinyl tape 3 times (6 layers) over half the width of the connection. | The connection was made using a plug-in connector, and the connecting portion was not wrapped with vinyl tape. | 1 | ['半幅(はんはば)- Half-width cloth', '厚さ(あつ)- Thickness', '終端(しゅうたん)- Terminus', '相互(そうご)- Mutual', '屋内配線(おくないはいせん)-Interior wiring '] | 600Vビニル{絶縁}ビニルシースケーブル平形1.6mmを{使用}した{低圧}{屋内配線}{工事}で、絶緑{電線}{相互}の{終端}{接続}{部分}の絶緑処理として、{不適切}なものは。 ただし、ビニルテープはJISに定める{厚さ}約0.2mmの{電気}{絶縁}用ポリ塩化ビニル粘着テープとする。 | リングスリーブ（E形）により{接続}し、{接続}{部分}を自己融着性{絶縁}テープ（{厚さ}約0.5mm）で{半幅}以上重ねて1回（2層）巻いた。 | リングスリーブ（E形）により{接続}し、{接続}{部分}を黒色粘着性ポリエチレン{絶縁}テープ（{厚さ}約0.5mm）で{半幅}以上重ねて3回（6層）巻いた。 | リングスリーブ（E形）により{接続}し、{接続}{部分}をビニルテープで{半幅}以上重ねて3回（6層）巻いた。 | 差込形{コネクタ}により{接続}し、{接続}{部分}をビニルテープで巻かなかった。 |  | 2020_2,
20 | What is the appropriate type of construction work depending on the facility location for indoor wiring with a working voltage of 100V? |  | Metal wire work in a dry place that cannot be inspected | Flat protection layer construction in a humid place where inspection is not possible | Lighting duct work in an open area with high humidity | Metal duct work in a dry place, even if it is an unfolded place | 4 | ['金属(きんぞく)- Metal', '湿気(しっけ)- Moisture', '隠蔽(いんぺい)- Concealment', '施設(しせつ)- Institution'] | {使用}{電圧}100Vの{屋内配線}の{施設}{場所}による{工事}の{種類}として、{適切}なものは。 | {点検}できない隠ぺい{場所}であって、乾燥した{場所}の{金属}{線}ぴ{工事} | {点検}できない隠ぺい{場所}であって、{湿気}の多い{場所}の平形保護層{工事} | 展開した{場所}であって、{湿気}の多い{場所}のライティングダクト{工事} | 展開した{場所}であって、乾燥した{場所}の{金属}ダクト{工事} |  | 2020_2,
21 | What is inappropriate as a method of indoor wiring work for installing a room air conditioner with a three-phase 200V, rated power consumption of 2.8kW in a house with a store? |  | Install simple contact protection measures for indoor wiring. | Install an earth leakage circuit breaker in the electric circuit. | In the electric circuit, a circuit breaker for wiring that is shared with the electric circuit of other loads will be installed. | The room air conditioner is installed by connecting directly to the indoor wiring. | 3 | ['接触(せっしょく)- Touch', '屋内配線(おくないはいせん)- Interior wiring', '定格(ていかく)- Rated value', '三相(さんそう)- Three phases'] | {店舗}付き{住宅}に{三相}200V、{定格}消費{電力}2.8kWのルームエアコンを{施設}する{屋内配線}{工事}の{方法}として、{不適切}なものは。 | {屋内配線}には、{簡易}{接触}{防護}{措置}を施す。 | {電路}には、{漏電}{遮断器}を{施設}する。 | {電路}には、他{負荷}の{電路}と共用の{配線}用{遮断器}を{施設}する。 | ルームエアコンは、{屋内配線}と{直接}{接続}して{施設}する。 |  | 2020_2,
22 | Inappropriate descriptions regarding class D grounding work on metal outer casings of machinery and equipment. |  | An electric circular saw was connected to the secondary circuit of a 3 kV·A isolation transformer (primary side 200 V, secondary side 100 V, secondary side ungrounded) and used without grounding. | An IV wire (annealed copper wire) with a diameter of 1.6 mm was used for the grounding wire of the three-phase 200 V rated output 0.75 kW motor outer case. | A multi-core cord with a cross-sectional area of ​​0.75 mm2 was used as the grounding wire for a single-phase 100 V mobile electric drill (single insulation). | A single-phase 100V motor with a rated output of 0.4kW was installed in a moist location, and a current-operated earth leakage breaker with a rated sensitivity current of 15mA and an operating time of 0.1 seconds was installed, eliminating grounding work | 4 | ['感度(かんど)- Sensitivity', '断面積(だんめんせき)- Cross-sectional area', '電気ドリル(でんき)- Electric drill', '直径(ちょっけい)- Diameter', '外箱(そとばこ)- Outer case', '出力(しゅつりょく)- Output', '電路(でんろ)- Electrical circuit', '金属製(きんぞくせい)- Made of metal', '機械(きかい)- Machine'] | {機械}{器具}の{金属}製{外箱}に施すD{種}{接地}{工事}、に関する{記述}で、{不適切}なものは。 | 一次側200V、二次側100V、3kV・Aの{絶縁}{変圧器}（二次側非{接地}）の二次側{電路}に電動丸のこぎりを{接続}し、{接地}を施さないで{使用}した。 | {三相}200V{定格}{出力}0.75kW{電動機}{外箱}の{接地}線に{直径}1.6mmのIV{電線}（軟{銅線}）を{使用}した。 | {単相}100V移動式の{電気}ドリル（一重{絶縁}）の{接地}{線}として多心コードの{断面積}0.75mm2の1心を{使用}した。 | {単相}100V{定格}{出力}0.4kWの{電動機}を{水気}のある{場所}に{設置}し、{定格}{感度}{電流}15mA、{動作時間}0.1秒の{電流}動作型{漏電}{遮断器}を取り付けたので、{接地}{工事}を{省略}した。 |  | 2020_2,
23 | What is the proper way to insert wires into metal tubes without creating electromagnetic imbalances? |  | Picture_23_A | Picture_23_B | Picture_23_C | Picture_23_D | 1 | ['電線(でんせん)- Electric line', '不平衡(ふへいこう)- Imbalance', '電磁的(でんじてき)- Electromagnetic'] | {電磁}的{不平衡}を生じないように、{電線}を{金属}{管}に挿入する{方法}として、{適切}なものは。 | Picture_23_A | Picture_23_B | Picture_23_C | Picture_23_D |  | 2020_2,
24 | What is the correct statement about the circuit meter (tester)? |  | When measuring AC or DC voltage with an analog method, select and use the range that is immediately higher than the assumed value in advance. | The output voltage at the terminals of the circuit meter when measuring resistance is an alternating voltage. | The digital type has a built-in battery, but the analog type does not require a battery. | We measured the resistance between the electric circuit and the ground. The measured value may be used as the insulation resistance value of the electric circuit. | 1 | ['電池(でんち)- Battery ', '端子(たんし)- Terminal ', '回路計(かいろけい)- Multimeter', '場合(ばあい)- Case; situation', '交流(こうりゅう)- Exchange'] | {回路}計（テスタ）に関する{記述}として、{正しい}ものは。 | アナログ式で{交流}又は{直流}{電圧}を{測定}する{場合}は、あらかじめ想定される{値}の直近上位のレンジを選定して{使用}する。 | 抵抗を{測定}する{場合}の{回路}計の{端子}における{出力}{電圧}は、{交流}{電圧}である。 | ディジタル式は{電池}を内蔵しているが、アナログ式は{電池}を{必要}としない。 | {電路}と{大地}間の抵抗{測定}を行った。その{測定}{値}は{電路}の{絶縁}抵抗{値}として{使用}してよい。 |  | 2020_2,
25 | In single-phase three-wire 100/200V indoor wiring, the minimum value of insulation resistance for each circuit that can be separated by a switch or overcurrent circuit breaker is stipulated in the "Ministerial Ordinance for Technical Standards for Electrical Equipment". What is the correct combination of values ​​[MΩ]? |  | 2 Between the wires: 0.4 | Between the circuit and the earth: 0.2 Between the wires: 0.2 | Between the circuit and the earth: 0.1 Between the wires: 0.1 | Between the circuit and the earth: 0.1 Between the wires: 0.2 | 4 | ['測定値(そくていち)- Measured value', '必要(ひつよう)- Necessary', '電圧(でんあつ)- Voltage', '測定(そくてい)- Measurement'] | {単相}3線式100/200Vの{屋内配線}において、{開閉器}又は過{電流}{遮断器}で区切ることができる{電路}ごとの{絶縁}抵抗の{最小}{値}として、「{電気}{設備}に関する{技術基準}を定める{省令}」に規定されている{値}［MΩ］の{組合せ}で、{正しい}ものは。 | {電路}と{大地}間：0.2 {電線}{相互}間：0.4 | {電路}と{大地}間：0.2 {電線}{相互}間：0.2 | {電路}と{大地}間：0.1 {電線}{相互}間：0.1 | {電路}と{大地}間：0.1 {電線}{相互}間：0.2 |  | 2020_2,
26 | When using a direct-reading earth resistance meter (earth tester) to measure the earth resistance by direct reading, what is the appropriate placement of the auxiliary earth electrodes (2 places)? |  | With the earth electrode to be measured at the end, place two auxiliary earth electrodes on a straight line with a distance of about 10m. | With the ground electrode to be measured in the center, place the auxiliary ground electrodes in line on the left and right with a distance of about 5 m. | With the earth electrode to be measured at the end, place two auxiliary earth electrodes on a straight line one after another about 1m apart. | Place the earth electrode to be measured and two auxiliary earth electrodes about 5m apart from each other in an equilateral triangle. | 1 | ['相互(そうご)- Mutual', '極(きょく)- Pole', '程度(ていど)- Standard', '接地(せっち)- Ground (electricity)'] | 直読式{接地}抵抗計（{アース}テスタ）を{使用}して直読で{接地}抵抗を{測定}する{場合}、{補助}{接地}{極}（2{箇所}）の{配置}として、{適切}なものは。 | 被{測定}{接地}{極}を端とし、一直{線}上に2{箇所}の{補助}{接地}{極}を順次10m{程度}離して{配置}する。 | 被{測定}{接地}{極}を{中央}にして、左右一直{線}上に{補助}{接地}{極}を5m{程度}離して{配置}する。 | 被{測定}{接地}{極}を端とし、一直{線}上に2{箇所}の{補助}{接地}{極}を順次1m{程度}離して{配置}する。 | 被{測定}{接地}{極}と2{箇所}の{補助}{接地}{極}を{相互}に5m{程度}離して正三角形に{配置}する。 |  | 2020_2,
27 | What is wrong about the purpose of continuity testing? |  | Check if the electric circuit is charged. | Detecting disconnections of wires to fixtures. | Find broken wires. | Determining whether the circuit connection is correct or not. | 2 | ['器具(きぐ)- Implement', '充電(じゅうでん)- Charging', '目的(もくてき)- Purpose'] | {導通}試験の{目的}として、誤っているものは。 | {電路}の{充電}の有無を{確認}する。 | {器具}への結{線}の未{接続}を発見する。 | {電線}の{断線}を発見する。 | {回路}の{接続}の正誤を判別する。 |  | 2020_2,
28 | Which of the following statements about electrical safety laws is incorrect? |  | The "Electrical Contractor Law" is a law that stipulates the qualifications and obligations of those engaged in electrical work. | The definition of electric facilities for general use is stipulated in the "Ministerial Ordinance for Establishing Technical Standards for Electrical Equipment" | The "Electrical Appliance and Material Safety Law" is a law aimed at preventing the occurrence of dangers and obstacles caused by electrical appliances by regulating the manufacture, sale, etc. of electrical appliances. | The "Electrical Appliance and Material Safety Law" stipulates that electricians must not use electrical appliances that are not labeled according to the law for electrical work. | 2 | ['発生(はっせい)- Occurrence', '危険(きけん)- Danger', '用品(ようひん)- Articles', '資格(しかく)- Qualifications', '定義(ていぎ)- Definition', '記述(きじゅつ)- Description', '保安(ほあん)- Security'] | {電気}の{保安}に関する{法令}についての{記述}として、誤っているものは。 | 「{電気}{工事}士法」は、{電気}{工事}の{作業}に{従事}する者の{資格}及び{義務}を定めた{法律}である。 | 一般用{電気}工{作物}の{定義}は、「{電気}{設備}に関する{技術基準}を定める{省令}」において定めている。 | 「{電気}{用品}安全法」は、{電気}{用品}の{製造}、{販売}等を規制することなどにより、{電気}{用品}による{危険}及び{障害}の{発生}を防止することを{目的}とした{法律}である。 | 「{電気}{用品}安全法」では、{電気}{工事}士は、{同法}に基づく{表示}のない{電気}{用品}を{電気}{工事}に{使用}してはならないと定めている。 |  | 2020_2,
29 | Under the Electrical Appliance and Material Safety Law, what is covered as a specific electrical appliance? |  | 25mm outer diameter metal conduit | Circuit breaker with rated current of 60A | Cable wiring switch box | Synthetic resin insulated wire with a nominal cross-sectional area of ​​150mm2 | 2 | ['合成樹脂(ごうせいじゅし)- Plastic', '特定(とくてい)- Specific'] | 「{電気}{用品}安全法」において、{特定}{電気}{用品}の{適用}を受けるものは。 | {外径}25mmの{金属}製{電線}{管} | {定格}{電流}60Aの{配線}用{遮断器} | ケーブル{配線}用{スイッチ}ボックス | {公称}{断面積}150mm2の{合成}樹脂{絶縁}{電線} |  | 2020_2,
30 | What is subject to the application of electric tools for general use. However, the power generation equipment shall have a voltage of 600V or less and shall be installed on the same premises. |  | A movie theater equipped with emergency internal combustion power generation equipment with a low-voltage power receiving capacity of 40 kW and an output of 15 kW | A machine shop with a high voltage power receiving capacity of 55 kW | A kindergarten equipped with solar power generation equipment with a low-voltage power receiving capacity of 40 kW and an output of 15 kW | A convenience store with a high-voltage power receiving capacity of 55 kW | 3 | ['高圧(こうあつ)- High Voltage', '映画館(えいがかん)- Movie theater', '受電(じゅでん)- Receiving electricity', '発電(はつでん)- Electricity generation', '適用(てきよう)- Applying'] | 一般用{電気}工{作物}の{適用}を受けるものは。 ただし、{発電}{設備}は{電圧}600V{以下}で、同一{構内}に{設置}するものとする。 | {低圧}{受電}で、{受電}{電力}の{容量}が40kW、{出力}15kWの非常用内燃力{発電}{設備}を備えた{映画館} | {高圧}{受電}で、{受電}{電力}の{容量}が55kWの{機械}{工場} | {低圧}{受電}で、{受電}{電力}の{容量}が40kW、{出力}15kWの太陽{電池}{発電}{設備}を備えた幼稚園 | {高圧}{受電}で、{受電}{電力}の{容量}が55kWのコンビニエンスストア |  | 2020_2,
31 | What is the pole arrangement (blade support) of the outlet shown in ①? |  | Picture_31_A | Picture_31_B | Picture_31_C | Picture_31_D | 2 | ['極(きょく)- Pole', '配置(はいち)- Arrangement '] | ①で{示す}{コンセント}の{極}{配置}（刃受）は。 | Picture_31_A | Picture_31_B | Picture_31_C | Picture_31_D |  | 2020_2,
32 | What is the installation location of the fixtures indicated by ②? |  | Patio surface | Wall surface | Bed surface | Double bed surface | 1 | ['器具(きぐ)- Appliance', '記号(きごう)- Symbol'] | ②で{示す}{図}{記号}の{器具}の取り付け{場所}は。 | {天井}面 | {壁面} | {床面} | 二重{床面} |  | 2020_2,
33 | What is the wiring method for the symbol shown in ③? |  | Concealed ceiling wiring | Concealed wall wiring | Concealed floor wiring | Exposed wiring | 3 | ['壁(かべ)- Wall', '画像(がぞう)- Image'] | ③で{示す}{図}{記号}の{配線}{方法}は。 | {天井}隠ぺい{配線} | {壁}隠ぺい{配線} | {床}隠ぺい{配線} | 露出{配線} |  | 2020_2,
34 | What kind of pipes are used in the wiring work for the part indicated by ? |  | Rigid PVC Conduit | Impact-resistant hard vinyl chloride conduit | Impact resistant rigid PVC pipe | Wave Fu Rigid Synthetic Resin Tube | 4 | ['種類(しゅるい)- Variety', '硬質(こうしつ)- Hardness', '問題(もんだい)- Question'] | ④で{示す}{部分}の{配線}{工事}で用いる{管}の{種類}は。 | {硬質}塩化ビニル{電線}{管} | 耐衝撃性{硬質}塩化ビニル{電線}{管} | 耐衝撃性{硬質}塩化ビニル{管} | 波付{硬質}{合成}樹脂{管} |  | 2020_2,
35 | What is the name of the instrument with the graphical symbol shown in ⑤? |  | Circuit breaker for wiring | Earth leakage breaker (with overload protection) | Motor breaker | Cutout switch | 2 | ['配線用遮断器(はいせんようしゃだんき)- MCCB', '記号(きごう)- Symbol'] | ⑤で{示す}{図}{記号}の{器具}の{名称}は。 | {配線}用{遮断器} | {漏電}{遮断器}（{過負荷}保護付） | モータブレーカ | カットアウト{スイッチ} |  | 2020_2,
| What is the minimum allowable value [MΩ] for the insulation resistance between the electric circuit and ground in the part indicated by ⑥? |  | 0.1 | 0.2 | 0.4 | 1 | 3 | ['最小値(さいしょうち)- Minimum value', '部分(ぶぶん)- Portion'] | ⑥で{示す}{部分}の{電路}と{大地}間との{絶縁}抵抗として、{許容}される{最小}{値}［MΩ］は。 | 0.1 | 0.2 | 0.4 | 1 |  | 2020_2,
| What is the name of the instrument with the graphical symbol shown in ⑦? |  | Electromagnetic switch | Push button switch | Remote control relay | Remote control selector switch | 3 | ['開閉器(かいへいき)- Switch', '電磁(でんじ)- Electromagnetic'] | ⑦で{示す}{図}{記号}の{器具}の{名称}は。 | {電磁}{開閉器} | 押しボタン{スイッチ} | リモコン{リレー} | リモコンセレクタ{スイッチ} |  | 2020_2,
38 | What is the correct combination of the type of grounding work shown in ⑧ and the minimum thickness of the grounding wire? |  | Class A grounding work Minimum thickness of grounding wire: 2.6mm | Class A grounding work Minimum thickness of grounding wire: 1.6mm | Class D grounding work Minimum thickness of grounding wire: 2.6mm | Class D grounding work Minimum thickness of grounding wire: 1.6mm | 4 | ['太い(ふと)- Thick', '種(たね)- Seed', '最小(さいしょう)- Minimum'] | ⑧で{示す}{部分}の{接地}{工事}の{種類}と{接地}{線}の{最小}太さの{組合せ}で、{正しい}ものは。 | A{種}{接地}{工事} {接地}{線}の{最小}太さ：2.6mm | A{種}{接地}{工事} {接地}{線}の{最小}太さ：1.6mm | D{種}{接地}{工事} {接地}{線}の{最小}太さ：2.6mm | D{種}{接地}{工事} {接地}{線}の{最小}太さ：1.6mm |  | 2020_2,
39 | What is the purpose of using the instrument with the symbol shown in ⑨? |  | Cut off the unbalanced current. | Cut off only the ground fault current. | Cut off overcurrent and ground fault current. | Cut off only overcurrent. | 4 |  | ⑨で{示す}{図}{記号}の{器具}を用いる{目的}は。 | {不平衡}{電流}を{遮断}する。 | 地絡{電流}のみを{遮断}する。 | 過{電流}と地絡{電流}を{遮断}する。 | 過{電流}のみを{遮断}する。 |  | 2020_2,
40 | What is the minimum height [m] above the ground surface of the spur line attachment point indicated by ⑩? However, the lead-in line shall not cross the road, it shall not be a technically unavoidable case, and it shall not hinder traffic. |  | 1 .2 | 2.5 | 3 | 3.5 | 2 | ['場合(ばあい)- Situation', '道路(どうろ)- Road', '高さ(たか)- Height'] | ⑩で{示す}引込{線}取付点の地表上の{高さ}の最低{値}［m］は。 ただし、引込{線}は{道}路を横断せず、技術上やむを得ない{場合}で、交通に支障がないものとする。 | 1 .2 | 2.5 | 3 | 3.5 |  | 2020_2,
41 | The one with the symbol shown in ⑪ |  | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D | 1 | ['記号(きごう)- Sign'] | ⑪で{示す}{図}{記号}のものは。 | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D |  | 2020_2,
42 | What is the combination used for the connection work of the part indicated by ⑫? |  | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D | 3 | ['作業(さぎょう)- Work', '接続(せつぞく)- Connection'] | ⑫で{示す}{部分}の{接続}{作業}に{使用}される{組合せ}は。 | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D |  | 2020_2,
43 | As for the equipment with the symbol shown in ⑬. |  | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D | 1 | ['器具(きぐ)- Tool; instrument'] | ⑬で{示す}{図}{記号}の{器具}は。 | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D |  | 2020_2,
44 | What is the equipment with the symbol shown in ⑭? |  | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D | 4 | ['図(ず)- Diagram; figure'] | ⑭で{示す}{図}{記号}の{器具}は。 | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D |  | 2020_2,
45 | If all the connections in the box indicated by ⑮ are plug-in connectors, what is the correct combination of the type of plug-in connectors to be used and the minimum number? However, the wire to be used shall be VVF1.6. |  | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D | 1 | ['電線(でんせん)- Electric line', '種類(しゅるい)- Variety; kind', '接続(せつぞく)- Connection'] | ⑮で{示す}ボックス内の{接続}をすべて差込形{コネクタ}とする{場合}、{使用}する差込形{コネクタ}の{種類}と{最少}{個数}の{組合せ}で、{正しい}ものは。ただし、{使用}する{電線}はVVF1.6とする。 | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D |  | 2020_2,
46 | What cables are necessary for the wiring work of the part indicated by ⑯? However, the number of core wires should be the minimum. |  | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D | 2 | ['必要(ひつよう)- Necessary', '最少(さいしょう)- Lowest; minimum'] | ⑯で{示す}{部分}の{配線}{工事}に{必要}なケーブルは。ただし、心線数は{最少}とする。 | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D |  | 2020_2,
47 | If all the connections in the box shown in ⑰ are crimped connections, what is the correct combination of ring sleeve type, number, and markings to be used? However, the wire to be used should be VVF1.6 unless otherwise specified. In addition, ○, small, and medium in the center of the ring sleeve shown in the photograph represent engravings. |  | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D | 3 | ['中央(ちゅうおう)- Centre', '種類(しゅるい)- Variety; kind', '個数(こすう)- Number of articles'] | ⑰で{示す}ボックス内の{接続}をすべて{圧着}{接続}とする{場合}、{使用}するリングスリーブの{種類}、{個数}及び{刻印}の{組合せ}で、{正しい}ものは。 ただし、{使用}する{電線}は{特記}のないものはVVF1.6とする。また、{写真}に{示す}リングスリーブ{中央}の○、小、中は{刻印}を表す。 | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D |  | 2020_2,
48 | Items that are not used for drilling holes in the distribution board (made of metal) shown in ⑱. |  | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D | 4 | ['穴あけ(あな)- Drilling', '分電盤(ぶんでんばん)- Distribution board'] | ⑱で{示す}{分電盤}（{金属}製）の{穴あけ}に{使用}されることのないものは。 | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D |  | 2020_2,
49 | An unused outlet is a symbol in this wiring diagram. |  | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D | 4 | ['記号(きごう)- Sign', '配線図(はいせんず)- Wiring diagram'] | この{配線}{図}の{図}{記号}で、{使用}されていない{コンセント}は。 | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D |  | 2020_2,
50 | What is the combination of the pull box used and the number of the symbols in this wiring diagram? |  | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D | 2 | ['組み合わせ(くみあわせ)- Combination', '個数(こすう) -Number of articles'] | この{配線}{図}の{図}{記号}で、{使用}されているプルボックスとその{個数}の{組合せ}は。 | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D |  | 2020_2,