## Sheet1
no | Eng | Picture | Option_1_Eng | Option_2_Eng | Option_3_Eng | Option_4_Eng | Ans | Vocab | Jpn | Option_1_Jpn | Option_2_Jpn | Option_3_Jpn | Option_4_Jpn | Exp | comment
1 | In the circuit shown in the figure, when the switch S is closed, the voltage [V] between terminals a and b is | Picture_1 | 45 | 60 | 75 | 120 | 2 | ['電圧(でんあつ)- Voltage', '回路(かいろ)- Circuit'] | {図}のような{回路}で、{スイッチ}Sを閉じたとき、a-b{端子}間の{電圧}［V］は。 | 45 | 60 | 75 | 120 | 30 [Ω] + 30 [Ω] = 60 [Ω] 100 [V]/60 [Ω] = 1.666 [A] 30 [Ω] x 1.666 [A] = 50 [V] | 2021_1,
2 | When a voltage V [V] is applied to a resistance R [Ω], a current I [A] flows and a power of P [W] is consumed. |  | PI/V | P/𝐼^2 | V^2/P | V/I | 1 | ['場合(ばあい)- Case; Situation', '電流(でんりゅう)- Electric current', '抵抗(ていこう)- Resistor'] | 抵抗R［Ω］に{電圧}V［V］を加えると、{電流}I［A］が流れ、P［W］の{電力}が消費される{場合}、抵抗R［Ω］を{示す}式として、誤っているものは。 | PI/V | P/𝐼^2 | V^2/P | V/I |  | 2021_1,
3 | Due to poor wire connection, the contact resistance at the connection point was 0.5Ω. When a current of 20A flows through this wire, the amount of heat [kJ] generated in one hour from the connection point is. However, the value of contact resistance should not change. |  | 72 | 144 | 720 | 1440 | 3 | ['熱量(ねつりょう)- Quantity of heat', '電流(でんりゅう)- Electric current', '接続(せつぞく)- Connection', '電線(でんせん)- Electric cable'] | {電線}の{接続}{不良}により、{接続}点の{接触}抵抗が0.5Ωとなった。この{電線}に20Aの{電流}が{流れる}と、{接続}点から1時間に{発生}する{熱量}［kJ］は。 ただし、{接触}抵抗の{値}は変化しないものとする。 | 72 | 144 | 720 | 1440 | 20 [A] x 20 [A] x 0.5 [Ω] x 3600 seconds = 720,000 [J] = 720 [kJ] | 2021_1,
4 | What is the power consumption [W] of a circuit in which resistance and reactance are connected in parallel as shown in the figure? | Picture_4 | 500 | 625 | 833 | 1042 | 2 | ['回路(かいろ)- Circuit', '並列(へいれつ)- Parallel'] | {図}のような抵抗とリアクタンスとが{並列}に{接続}された{回路}の消費{電力}［W］は。 | 500 | 625 | 833 | 1042 | IR = V/R IR = 100/16 = 6.25A. P＝(IR)²×R P = 6.25² x 16 P=39.0625×16=625w | 2021_1,
5 | In the three-phase three-wire 200V circuit as shown in the figure, the resistance between c and o was broken. What is the correct combination of voltage V value [V] between a and a before and after disconnection? | Picture_5 | Before disconnection: 116 , After disconnection: 116 | Before disconnection: 116, After disconnection: 100 | Before disconnection: 100 After disconnection: 116 | Before disconnection: 100 After disconnection: 100 | 2 | ['値(あたい)- Value', '断線(だんせん)- Disconnection', '回路(かいろ)- Circuit', '三相(さんそう)- Three phases'] | {図}のような{三相}3線式200Vの{回路}で、c-o間の抵抗が{断線}した。{断線}前と{断線}後のa-o間の{電圧}Vの{値}［V］の{組合せ}として、{正しい}ものは。 | {断線}前116、{断線}後116 | {断線}前116、{断線}後100 | {断線}前100、{断線}後116 | {断線}前100、{断線}後100 | Phase voltage = line voltage/√3. Phase voltage = 200/√3 = 115.6069...≒116V A single-phase 200V circuit is formed. Therefore, 200V is divided into. The voltage across ao will be 100V. | 2021_1,
6 | In the single-phase three-wire circuit as shown in the figure, the indicated value I1 [A] of the ammeter (A) when only the switch a is closed and the indicated value of the ammeter (A) when the switches a and b are closed. What is the appropriate combination of I2 [A]? However, (H) is an electric heater with a rated voltage of 100V. | Picture_6 | I1：2 I2：2 | I1：2 I2：0 | I1：2 I2：4 | I1：4 I2：0 | 2 | ['定格(ていかく)- Rated value', '電熱器(でんねつき)- Electrothermic equipment', '電流計(でんりゅうけい)- Ammeter'] | {図}のような{単相}3{線}式{回路}で、{スイッチ}aだけを閉じたときの{電流}計（A）の{指示}{値}I1［A］と{スイッチ}a及びbを閉じたときの{電流}計（A）の{指示}{値}I2［A］の{組合せ}として、{適切}なものは。 ただし、（H）は{定格}{電圧}100Vの{電熱器}である。 | I1：2 I2：2 | I1：2 I2：0 | I1：2 I2：4 | I1：4 I2：0 |  | 2021_1,
7 | In a three-phase AC circuit as shown in the figure, when the resistance per wire is 0.2Ω and the line current is 15A, the power loss [W] of this line is. | Picture_7 | 78 | 90 | 120 | 135 | 4 | ['電力損失(でんりょくそんしつ)- Electric power loss', '線(せん)- Line'] | {図}のような{三相}{交流}{回路}において、{電線}1線{当たり}の抵抗が0.2Ω、線{電流}が15Aのとき、この{電線}路の{電力}損失［W］は。 | 78 | 90 | 120 | 135 | This is the power loss in the wire, (P = I²R) The power loss for three lines = P = 3I²R. P = 3I²R P = 3 x 15² x 0.2 P = 3 x 225 x 0.2 = 135w | 2021_1,
8 | When installing seven 600V vinyl insulated wires (annealed copper wires) with a cross-sectional area of 5.5 mm2 in a low-pressure indoor wiring system using synthetic resin flexible wire pipes (PF pipes), the permissible current per wire [ A] is. However, the ambient temperature shall be 30° C or less, and the current reduction coefficient shall be 0.49. |  | 13 | 17 | 24 | 29 | 3 | ['減少(げんしょう)- Decrease', '許容(きょよう)- Permission', '工事(こうじ)- Construction work', '低圧(ていあつ)- Low voltage'] | {合成}樹脂製可とう{電線}管（PF管）による{低圧}{屋内配線}{工事}で、{管内}に{断面積}5.5mm2の600Vビニル{絶縁}{電線}（軟{銅線}）7本を収めて{施設}した{場合}、{電線}1本{当たり}の{許容}{電流}［A］は。 ただし、{周囲}{温度}は30°C{以下}、{電流}{減少}{係数}は0.49とする。 | 13 | 17 | 24 | 29 | The allowable current value of a 600 [V] vinyl insulated wire (annealed copper wire) with a cross-sectional area of ​​5.5 [mm] is It is 49 [A] of stranded wire. 49 [A] x 0.49 = 24.01 [A] | 2021_1,
9 | As shown in the figure, there is a single-phase two-wire low-voltage indoor trunk line connected to one electric heater (H) and two electric motors (M). What is the appropriate combination of the current IW [A] that determines the thickness of the main line and the current IB [A] that determines the rated current of the overcurrent circuit breaker that must be installed in the main line? . However, the demand rate is assumed to be 100%. | Picture_9 | IW 50 IB 125 | IW 50 IB 130 | IW 60 IB 130 | IW 60 IB 150 | 3 | ['定格(ていかく)- Rated value', '遮断器(しゃだんき)- Circuit breaker', '電流(でんりゅう)- Electric current', '幹線(かんせん)- Main line', '根拠(こんきょ)- Grounds'] | {図}のような{電熱器}（H）1台と{電動機}（M）2台が{接続}された{単相}2線式の{低圧}{屋内}{幹線}がある。この{幹線}の太さを決定する{根拠}となる{電流}IW［A］と{幹線}に{施設}しなければならない過{電流}{遮断器}の{定格}{電流}を決定する{根拠}となる{電流}IB［A］の{組合せ}として、{適切}なものは。 ただし、{需要}率は100%とする。 | IW 50 IB 125 | IW 50 IB 130 | IW 60 IB 130 | IW 60 IB 150 | H0 = 10A M0 = 20A + 20A = 40A Since M0 = 40A, multiply by 1.25, 40A x 1.25 = 50A This is the sum of the motor sum multiplied by 3 and the heater sum. Since it becomes M0×3+H0, 40 x 3 + 10 = 130A. | 2021_1,
10 | In the design of branch circuits for low-voltage indoor wiring, what is the appropriate combination of circuit breakers, branch circuit wire thicknesses, and outlets? However, the distance from the branch point to the circuit breaker for wiring is 3 m, and the distance from the circuit breaker for wiring to the outlet is 8 m. Furthermore, outlets must not be dual-use. |  | Picture_10_A | Picture_10_B | Picture_10_C | Picture_10_D | 1 | ['回路(かいろ)- Circuit', '低圧(ていあつ)- Low voltage', '設計(せっけい)- plan'] | {低圧}{屋内配線}の{分岐}{回路}の{設計}で、配線用{遮断器}、{分岐}{回路}の{電線}の太さ及び{コンセント}の{組合せ}として、{適切}なものは。 ただし、{分岐}点から配線用{遮断器}までは3m、配線用{遮断器}から{コンセント}までは8mとし、{電線}の{数値}は{分岐}{回路}の{電線}（軟鋼線）の太さを{示す}。 また、{コンセント}は{兼用}{コンセント}ではないものとする。 | Picture_10_A | Picture_10_B | Picture_10_C | Picture_10_D |  | 2021_1,
11 | What is the purpose of using the entrance cap? |  | It is mainly used to prevent rainwater from entering by attaching it to the upper end of a vertical metal pipe. | Used to prevent concrete from entering the metal pipe when concrete is poured. | Used for parts where pipes bend at right angles in metal pipe work. | Used to block the end of the floor duct | 1 | ['直角(ちょっかく)- Right angle', '金属(きんぞく)- Metal'] | エン{トランス}キャップの{使用}{目的}は。 | 主として垂直な{金属}{管}の上端部に取り付けて、雨水の浸入を防止するために{使用}する。 | コンクリート打ち込み時に{金属}{管内}にコンクリートが浸入するのを防止するために{使用}する。 | {金属}{管}{工事}で{管}が{直角}に屈曲する{部分}に{使用}する。 | フロアダクトの{終端部}を閉そくするために{使用}する。 |  | 2021_1,
12 | Which one has the best heat resistance? |  | 600V Class 2 vinyl insulated wire | 600V vinyl insulated wire | MI cable | 600V vinyl insulated vinyl sheath cable | 3 | ['絶縁(ぜつえん)- Insulation', '耐熱性(たいねつせい)- Thermostability'] | {耐熱性}が最も優れているものは。 | 600V二{種}ビニル{絶縁}{電線} | 600Vビニル{絶縁}{電線} | MIケーブル | 600Vビニル{絶縁}ビニルシースケーブル |  | 2021_1,
13 | What is the appropriate combination of the type of electrical work and the tools used for that work? |  | Synthetic resin pipe work and lead type thread cutter | Lighting duct work and synthetic resin pipe cutter | Metal pipe work and pipe bender | Metal wire work and bolt clipper | 3 | ['工事(こうじ)- Construction work', '種類(しゅるい)- Variety'] | {電気}{工事}の{種類}とその{工事}に{使用}する{工具}との{組合せ}で、{適切}なものは。 | {合成}樹脂{管}{工事}とリード型ねじ切り器 | ライティングダクト{工事}と{合成}樹脂{管}用カッタ | {金属}{管}{工事}とパイプベンダ | {金属}{線}ぴ{工事}とボルトクリッパ |  | 2021_1,
14 | When using a three-phase squirrel-cage induction motor with 6 poles at a frequency of 60Hz, the nearest rotational speed [min-1] is? |  | 600 | 1200 | 1800 | 3600 | 2 | ['周波数(しゅうはすう)- Frequency', '極(きょく)- pole'] | {極}数6の{三相}かご形{誘導電動機}を{周波数}60Hzで{使用}するとき、最も近い{回転}{速度}［min-1は。 | 600 | 1200 | 1800 | 3600 |  | 2021_1,
15 | What is wrong as a description about straight tube LED lamps. |  | Can be used as-is for all fluorescent lighting fixtures. | Low power consumption compared to fluorescent lamps with the same brightness. | Some have built-in controllers and some do not. | Long service life compared to fluorescent lamps. | 1 | ['使用(しよう)- Use; application', '比較(ひかく)- Comparison', '記述(きじゅつ)- Description', '同じ(おな)- Same'] | 直{管}LEDランプに関する{記述}として、誤っているものは。 | すべての{蛍光灯}照明{器具}にそのまま{使用}できる。 | {同じ}明るさの{蛍光灯}と{比較}して消費{電力}が小さい。 | 制御装置が内蔵されているものと内蔵されていないものとがある。 | {蛍光灯}に比べて寿命が長い。 |  | 2021_1,
16 | What is the name of the material shown in the photo? | Picture_16 | inorganic insulated cable | 600V Vinyl Insulated Vinyl Sheath Cable Flat | 600V cross-linked polyethylene insulated vinyl sheath cable | 600V Polyethylene Insulated Flame Resistant Polyethylene Sheath Cable Flat | 4 | ['耐燃性(たいねんせい)- Flame resistance', '画像(がぞう)- Image', '材料(ざいりょう)- Materials'] | {写真}に{示す}{材料}の{名称}は。 | 無機{絶縁}ケーブル | 600Vビニル{絶縁}ビニルシースケーブル平形 | 600V{架橋}ポリエチレン{絶縁}ビニルシースケーブル | 600Vポリエチレン{絶縁}{耐燃性}ポリエチレンシースケーブル平形 |  | 2021_1,
17 | The photo shows the name of the appliance. | Picture_17 | Earth leakage alarm | Electromagnetic switch | Wiring circuit breaker (for motor protection) | Earth leakage circuit breaker | 3 | ['漏電(ろうでん)- Leakage', '問題(もんだい)- Problem', '器具(きぐ)- Utensil'] | {写真}に{示す}{器具}の{名称}は。 | {漏電}{警報器} | {電磁}{開閉器} | {配線}用{遮断器}（{電動機}保護{兼用}） | {漏電}{遮断器} |  | 2021_1,
18 | The name of the tool shown in the photo is | Picture_18 | Manual hydraulic crimper | Manual hydraulic cutter | Knockout puncher (hydraulic) | Manual hydraulic compressor | 4 | ['圧縮機(あっしゅくき)- Compressor', '手動(しゅどう)- Manual', '工具(こうぐ)- Hand tool'] | {写真}に{示す}{工具}の{名称}は。 | {手動}油圧式{圧着}器 | {手動}油圧式カッタ | ノックアウトパンチャ（油圧式） | {手動}油圧式圧縮器 |  | 2021_1,
19 | The following table shows whether single-phase 100V indoor wiring can be installed by facility location and construction type. From a to f in the table, which is the correct combination of all the items that cannot be used as a facility? | Picture_19 | a, f | eのみ | bのみ | e, f | 2 | ['施設(しせつ)- Construction', '単相(たんそう)- Single phase'] | 次表は{単相}100V{屋内配線}の{施設}{場所}と{工事}の{種類}との{施工}の可否を{示す}表である。表中のa～fのうち、「{施設}できない」ものを{全て}選んだ{組合せ}として、{正しい}ものは。 | a, f | eのみ | bのみ | e, f |  | 2021_1,
20 | What is the appropriate construction method for cable construction using 600V vinyl-insulated vinyl-sheathed cable for low-voltage indoor wiring work (excluding temporary wiring work)? |  | Installed vertically along the side of the building material at the place where contact protection measures were taken, and the distance between the support points was 8m. | Housed in the same synthetic resin tube together with a low-current telephone wire without a metal shielding layer. | Buried directly in the concrete wall of the building. | A round cable was bent with the inside radius of the bending portion being 8 times the outside diameter of the cable. | 4 | ['外径(がいけい)- Outer diameter', '内側(うちがわ)- Inside', '距離(きょり)- Distance', '措置(そち)- Measure'] | {低圧}{屋内配線}{工事}（臨時配線{工事}の{場合}を除く）で、600Vビニル{絶縁}ビニルシースケーブルを用いたケーブル{工事}の{施工}{方法}として、{適切}なものは。 | {接触}{防護}{措置}を施した{場所}で、造営材の側面に沿って垂直に取り付け、その支持点間の{距離}を8mとした。 | {金属}製遮へい層のない{電話}用弱{電流}{電線}と共に同一の{合成}樹脂{管}に収めた。 | 建{物の}コンクリート{壁}の中に{直接}埋設した。 | 丸形ケーブルを、屈曲部の{内側}の半径をケーブル{外径}の8倍にして曲げた。 |  | 2021_1,
21 | What is the most appropriate construction method for electrically connecting metal pipes and outlet boxes in metal pipe work? |  | Picture_21_A | Picture_21_B | Picture_21_C | Picture_21_D | 3 | ['適切(てきせつ)- Appropriate', '方法(ほうほう)- Method'] | {金属}{管}{工事}で{金属}{管}とアウトレットボックスとを{電気}的に{接続}する{方法}として、{施工}上、最も{適切}なものは。 | Picture_21_A | Picture_21_B | Picture_21_C | Picture_21_D |  | 2021_1,
22 | In low-voltage indoor wiring by cable construction, there were four locations a to d where cables and low-current wires approached or intersected. What is the correct combination of all the appropriate ones selected from a to d? A: There was contact at the point where it crossed the low-current wire. B: The length of contact overlapping with the low-current wire was 3m. C: Installed at a distance of 10 cm to prevent contact with low-current wires. D: It was installed with a strong bulkhead to prevent contact with low-current power lines. |  | d のみ | c, d | b, c, d | a, b, c, d | 2 | ['全て(すべ)- Everything', '電流(でんりゅう)- Electric current', '離隔(りかく)- Isolation', '低圧_(ていあつ)- Low voltage'] | ケーブル{工事}による{低圧}{屋内配線}で、ケーブルと弱{電流}{電線}の{接近}又は交差する{箇所}が a ～ d の4{箇所}あった。a ～ d のうちから{適切}なものを{全て}選んだ{組合せ}として、{正しい}ものは。 a：弱{電流}{電線}と交差する{箇所}で{接触}していた。 b：弱{電流}{電線}と重なり合って{接触}している{長さ}が3mあった。 c：弱{電流}{電線}と{接触}しないように{離隔}{距離}を10cm離して{施設}していた。 d：弱{電流}{電線}と{接触}しないように堅ろうな隔{壁}を設けて{施設}していた。 | d のみ | c, d | b, c, d | a, b, c, d |  | 2021_1,
23 | Inappropriate work for metal flexible conduits for low-voltage indoor wiring (the conduits used shall be type 2 metal flexible conduits). |  | The bending radius of the inside of the tube is set to 6 times or more of the inner diameter of the tube. | A 600V vinyl insulated wire was placed inside the pipe. | A straight box connector was used to connect the tube and the box. | TS couplings were used to connect pipes and metal pipes (steel conduits). | 4 | ['鋼製(こうせい)- Made of steel', '内径(ないけい)- Inside diameter', '内側(うちがわ)- Inside'] | {低圧}{屋内配線}の{金属}可とう{電線}{管}（{使用}する{電線}{管}は2{種}{金属}製可とう{電線}{管}とする）{工事}で、{不適切}なものは。 | {管}の{内側}の曲げ半径を{管}の{内径}の6倍以上とした。 | {管内}に600Vビニル{絶縁}{電線}を収めた。 | {管}とボックスとの{接続}にストレートボックス{コネクタ}を{使用}した。 | {管}と{金属}{管}（{鋼製}{電線}{管}）との{接続}にTSカップリングを{使用}した。 |  | 2021_1,
24 | What is the correct combination of measuring instruments for use in low-voltage circuits and their applications? |  | Confirmation of voltage detector and electric circuit charge | Checking the tachometer and the phase order (phase rotation) of the three-phase circuit | Circuit meter (tester) and measurement of insulation resistance | Wattmeter and power consumption measurement | 1 | ['測定(そくてい)- Measurement', '確認(かくにん)- Confirmation', '回路計(かいろけい)- Multimeter', '検電器(けんでんき)- Voltage tester'] | {低圧}{電路}で{使用}する{測定}器とその{用途}の{組合せ}として、{正しい}ものは。 | {検電器}と{電路}の{充電}の有無の{確認} | {回転}計と{三相}{回路}の相順（相{回転}）の{確認} | {回路}計（テスタ）と{絶縁}抵抗の{測定} | {電力}計と消費{電力}量の{測定} |  | 2021_1,
25 | The following table shows the working voltage of a low-voltage circuit separated by a switch or overcurrent circuit breaker in a place where electricity is used and the minimum value of insulation resistance between wires and between the circuit and the ground. Which is the correct combination of numbers that applies to the following blanks (A), (B) and (C)? | Picture_25 | （A）0.1 （B）0.2 （C）0.3 | （A）0.1 （B）0.2 （C）0.4 | （A）0.2 （B）0.3 （C）0.4 | （A）0.2 （B）0.4 （C）0.6 | 2 |  | 次表は、{電気}{使用}{場所}の{開閉器}又は過{電流}{遮断器}で区切られる{低圧}{電路}の{使用}{電圧}と{電線}{相互}間及び{電路}と{大地}との間の{絶縁}抵抗の{最小}値についての表である。 次の空欄（A）、（B）及び（C）に当てはまる{数値}の{組合せ}として、{正しい}ものは。 | （A）0.1 （B）0.2 （C）0.3 | （A）0.1 （B）0.2 （C）0.4 | （A）0.2 （B）0.3 （C）0.4 | （A）0.2 （B）0.4 （C）0.6 |  | 2021_1,
26 | When measuring earth resistance using a direct-reading earth resistance meter, what is the appropriate placement of the two auxiliary earth electrodes P (for voltage) and C (for current) with respect to the earth electrode E to be measured? |  | Picture_26_A | Picture_26_B | Picture_26_C | Picture_26_D | 2 | ['配置(はいち)- Arrangement', '適切(てきせつ)- Appropriate', '補助(ほじょ)- Assistance', '場合(ばあい)- Case; situation'] | 直読式{接地}抵抗計を用いて、{接地}抵抗を{測定}する{場合}、被{測定}{接地}{極}Eに対する、2つの{補助}{接地}{極} P（{電圧}用）及び C（{電流}用）の{配置}として、{適切}なものは。 | Picture_26_A | Picture_26_B | Picture_26_C | Picture_26_D |  | 2021_1,
27 | What is the correct wiring method for a voltmeter, an ammeter, and wattmeter in a circuit from a single-phase AC power supply to a load? |  | Picture_27_A | Picture_27_B | Picture_27_C | Picture_27_D | 4 | ['結線(けっせん)- Hard wiring', '電圧計(でんあつけい)- Voltmeter', '回路(かいろ)- Circuit', '単相(たんそう)- Single phase'] | {単相}{交流}{電源}から{負荷}に至る{回路}において、{電圧}計、{電流}計、{電力}計の結{線}{方法}として、{正しい}ものは。 | Picture_27_A | Picture_27_B | Picture_27_C | Picture_27_D |  | 2021_1,
28 | According to the "Electrical Construction Professionals Act", the construction or work of general electric facilities that can only be engaged in by electricians. |  | Work to connect the cord to the plug-in connector | Work to attach the switchboard to the construction material | Work to install underdrains for underground cables | Wiring work on the secondary side of small transformers (secondary voltage is 36V or less) used for fire detectors | 2 | ['小型(こがた)- Small-sized', '作業(さぎょう)- Work; Operation', '従事(じゅうじ)- Being involved in'] | 「{電気}{工事}士法」において、一般用{電気}工{作物}の{工事}又は{作業}で{電気}{工事}士でなければ{従事}できないものは。 | 差込み{接続}器にコードを{接続}する{工事} | {配電盤}を造営材に取り付ける{作業} | {地中}{電線}用の暗きょを{設置}する{工事} | 火災感知器に{使用}する{小型}{変圧器}（二次{電圧}が36V{以下}）二次側の{配線}{工事} |  | 2021_1,
29 | Of the following electrical appliances to which the "Electrical Appliance and Material Safety Law" applies, the specified electrical appliances are: |  | Circuit breaker for wiring with a rated current of 20A | Ventilation fan with power consumption of 30W | Metal conduit tube with an outer diameter of 19 mm | Electric stove with power consumption of 1 kW | 1 | ['外径(がいけい)- Outer diameter', '適用(てきよう)- applying'] | 「{電気}{用品}安全法」の{適用}を受ける次の{電気}{用品}のうち、{特定}{電気}{用品}は。 | {定格}{電流}20Aの{配線}用{遮断器} | 消費{電力}30Wの換気扇 | {外径}19mmの{金属}製{電線}{管} | 消費{電力}1kWの{電気}ストーブ |  | 2021_1,
30 | Items that are not subject to the application of electric facilities for general use However, the power generation equipment must have a voltage of 600V or less and must be installed in a single location. |  | A movie theater equipped with emergency internal combustion power generation equipment with a low-voltage power receiving capacity of 35 kW and an output of 15 kW | A farm with a low-voltage power receiving capacity of 35 kW and a wind power generation facility with an output of 5 kW electrically connected to a solar power generation facility with an output of 10 kW. | A convenience store equipped with fuel cell power generation equipment with a low-voltage power receiving capacity of 45 kW and an output of 5 kW. | A kindergarten equipped with a solar cell power generation facility with a low-voltage power receiving capacity of 35 kW and an output of 15 kW. | 1 | ['電力(でんりょく)- Electric power', '映画館(えいがかん)- Movie theater', '容量(ようりょう)- Capacity', '発電(はつでん)- Electricity generation'] | 一般用{電気}工{作物}の{適用}を受けないものは。 ただし、{発電}{設備}は{電圧}600V{以下}で、1{構内}に{設置}するものとする。 | {低圧}{受電}で、{受電}{電力}の{容量}が35kW、{出力}15kWの非常用内燃力{発電}{設備}を備えた{映画館} | {低圧}{受電}で、{受電}{電力}の{容量}が35kW、{出力}10kWの太陽{電池}{発電}{設備}と{電気}的に{接続}した{出力}5kWの風力{発電}{設備}を備えた農園 | {低圧}{受電}で、{受電}{電力}の{容量}が45kW、{出力}5kWの燃料{電池}{発電}{設備}を備えたコンビニエンスストア | {低圧}{受電}で、{受電}{電力}の{容量}が35kW、{出力}15kWの太陽{電池}{発電}{設備}を備えた幼稚園 |  | 2021_1,
31 | What is the name of the device indicated by the symbol ①? |  | Chime | Time switch | Bell | Buzzer | 1 | ['画像(がぞう)- Image', '記号(きごう)- Symbol; code'] | ①で{示す}{図}{記号}の{機器}の{名称}は。 | チャイム | タイム{スイッチ} | ベル | ブザー |  | 2021_1,
32 | What is the maximum voltage [V] that can be used in the small force circuit shown in ②? |  | 24 | 30 | 48 | 60 | 4 | ['勢力(せいりょく)- Influence; power', '部分(ぶぶん)- Portion'] | ②で{示す}{部分}の小{勢力}{回路}で{使用}できる{電圧}の{最大値}［V］は。 | 24 | 30 | 48 | 60 |  | 2021_1,
33 | What is the type of low-voltage cable indicated by ③? |  | 600V Vinyl Insulated Vinyl Sheath Cable Round | 600V cross-linked polyethylene insulated vinyl sheath cable (single-core 3 strands) | 600V Vinyl Insulated Vinyl Sheath Cable Flat | 600V cross-linked polyethylene insulated vinyl sheath cable | 2 | ['円形(えんけい)- Round Shape', '絶縁(ぜつえん)- Insulation'] | ③で{示す}{低圧}ケーブルの{種類}は。 | 600Vビニル{絶縁}ビニルシースケーブル丸形 | 600V{架橋}ポリエチレン{絶縁}ビニルシースケーブル（単心3本のより{線}） | 600Vビニル{絶縁}ビニルシースケーブル平形 | 600V{架橋}ポリエチレン{絶縁}ビニルシースケーブル |  | 2021_1,
34 | What is the type of equipment for the symbol shown in ④? |  | Flasher with built-in position indicator light | Flasher with built-in confirmation indicator light | Hot-wire automatic switch | Delay switch | 1 | ['表示灯(ひょうじとう)- signal light', '点滅器(てんめつき)- Switch', '位置(いち)- Position'] | ④で{示す}{図}{記号}の{器具}の{種類}は。 | {位置}{表示}灯を内蔵する{点滅器} | {確認}{表示}灯を内蔵する{点滅器} | 熱{線}式{自動}{スイッチ} | {遅延}{スイッチ} |  | 2021_1,
35 | The pole arrangement (blade support) of the outlet indicated by ⑤ is |  | Picture_35_A | Picture_35_B | Picture_35_C | Picture_35_D | 2 |  | ⑤で{示す}{コンセント}の{極}{配置}（刃受）は。 | Picture_35_A | Picture_35_B | Picture_35_C | Picture_35_D |  | 2021_1,
36 | The part indicated by ⑥ is the outdoor unit of the room air conditioner. The sidenote indication of the graphic symbol is |  | O | B | I | R | 1 | ['表示(ひょうじ)- Indication', '部分(ぶぶん)- Portion'] | ⑥で{示す}{部分}はルームエアコンの{屋外}ユニットである。その{図}{記号}の傍記{表示}は。 | O | B | I | R |  | 2021_1,
37 | What is the maximum value [A] of the rated current of the equipment shown in ⑦? |  | 15 | 20 | 30 | 40 | 2 | ['最大値(さいだいち)- Greatest value', '電流(でんりゅう)- Electric current'] | ⑦で{示す}{機器}の{定格}{電流}の{最大値}［A］は。 | 15 | 20 | 30 | 40 |  | 2021_1,
38 | What is the allowable minimum value [MΩ] for the insulation resistance between the electric circuit and the ground in the part indicated by ⑧? |  | 0.1 | 0.2 | 0.4 | 1 | 1 | ['絶縁抵抗(ぜつえんていこう)- insulation resistance', '電路(でんろ)- Electrical circuit'] | ⑧で{示す}{部分}の{電路}と{大地}間の{絶縁}抵抗として、{許容}される{最小}{値}［MΩ］は。 | 0.1 | 0.2 | 0.4 | 1 |  | 2021_1,
39 | Attach the incandescent lamp to the fixture indicated by ⑨ by hanging it with a cord. What is the correct combination of codes and minimum cross-sectional area that can be used? |  | Vinyl cord 1.25mm2 | Vinyl cabtyre cord 0.75mm2 | Round rubber cord 0.75mm2 | Bag rubber cord 0.5mm2 | 3 | ['最小(さいしょう)- Smallest', '使用(しよう)- Use; application', '器具(きぐ)- Tool; instrument'] | ⑨で{示す}{器具}にコード吊りで{白熱電球}を取り付ける。{使用}できるコードと{最小}{断面積}の{組合せ}として、{正しい}ものは。 | ビニルコード 1.25mm2 | ビニルキャブタイヤコード 0.75mm2 | 丸打ちゴムコード 0.75mm2 | 袋打ちゴムコード 0.5mm2 |  | 2021_1,
40 | What is the minimum number of wires (number of core wires) of the part indicated by ⑩? |  | 2 | 3 | 4 | 5 | 1 | ['本数(ほんすう)- Number', '電線(でんせん)- Electric cable'] | ⑩で{示す}{部分}の{最少}{電線}{本数}（心線数）は。 | 2 | 3 | 4 | 5 |  | 2021_1,
41 | The equipment with the symbol shown in ⑪. |  | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D | 3 | ['機器(きき)- Device', '記号(きごう)- Symble'] | ⑪で{示す}{図}{記号}の{機器}は。 | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D |  | 2021_1,
42 | Those that will not be used in the construction of the part indicated by ⑫. |  | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D | 2 | ['工事(こうじ)- Construction work', '部分(ぶぶん)- Portion'] | ⑫で{示す}{部分}の{工事}において、{使用}されることのないものは。 | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D |  | 2021_1,
43 | Equipment with a graphical symbol shown in ⑬ |  | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D | 4 | ['図(ず)- Drawing'] | ⑬で{示す}{図}{記号}の{器具}は。 | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D |  | 2021_1,
44 | What is the correct combination of measuring instruments for checking the voltage and polarity of the outlet shown in ⑭? |  | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D | 2 | ['測定器(そくていき)- Measuring instrument', '極性(きょくせい)- Polarity', '電圧(でんあつ)- Voltage'] | ⑭で{示す}{コンセント}の{電圧}と{極}性を{確認}するための{測定}器の{組合せ}で、{正しい}ものは。 | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D |  | 2021_1,
45 | The equipment with the symbol shown in ⑮. |  | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D | 3 | ['記号(きごう)- Sign ', '機器(きき)- Equipment'] | ⑮で{示す}{図}{記号}の{機器}は。 | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D |  | 2021_1,
46 | When all the connections in the box shown in ⑯ ​​are crimped, what is the correct combination of ring sleeve type, number, and stamp after the crimped connection? All wires used, however, must be VVF1.6. In addition, O, small, and medium in the center of the ring sleeve shown in the photo represent engravings. |  | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D | 2 | ['電線(でんせん)- Cable', '圧着(あっちゃく)- Crimping', '種類(しゅるい)- Variety; kind', '接続(せつぞく)- Connection'] | ⑯で{示す}ボックス内の{接続}をすべて{圧着}{接続}した{場合}のリングスリーブの{種類}、{個数}及び{圧着}{接続}後の{刻印}との{組合せ}で、{正しい}ものは。 ただし、{使用}する{電線}はすべてVVF1.6とする。また、{写真}に{示す}リングスリーブ{中央}のO、小、中は{刻印}を表す。 | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D |  | 2021_1,
47 | If all the connections in the box shown in ⑰ are crimp connections, what is the correct combination of the type of ring sleeve to be used and the minimum number? All wires used, however, must be VVF1.6. |  | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D | 3 | ['種類(しゅるい)- Variety; kind', '個数(こすう)- Quantity', '接続(せつぞく)- Connection'] | ⑰で{示す}ボックス内の{接続}をすべて{圧着}{接続}とする{場合}、{使用}するリングスリーブの{種類}と{最少}{個数}の{組合せ}で、{正しい}ものは。 ただし、{使用}する{電線}はすべてVVF1.6とする。 | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D |  | 2021_1,
48 | If all the connections in the box indicated by ⑱ are plug-in connectors, what is the correct combination of the type of plug-in connectors to be used and the minimum number? All wires used, however, must be VVF1.6. |  | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D | 2 | ['場合(ばあい)- Case; situation', '個数(こすう)- Quantity'] | ⑱で{示す}ボックス内の{接続}をすべて差込形{コネクタ}とする{場合}、{使用}する差込形{コネクタ}の{種類}と{最少}{個数}の{組合せ}で、{正しい}ものは。 ただし、{使用}する{電線}はすべてVVF1.6とする。 | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D |  | 2021_1,
49 | From the symbols in this wiring diagram, which outlets are not used in this construction. |  | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D | 4 | ['工事(こうじ)- Construction work', '配線図(はいせんず)- Wiring diagram'] | この{配線}{図}の{図}{記号}から、この{工事}で{使用}されていない{コンセント}は。 | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D |  | 2021_1,
50 | From the symbols in this wiring diagram, which switch is not used in this construction? However, the diagram below the photo shows the configuration of the contacts. |  | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D | 3 | ['記号(きごう)- Sign ', '接点(せってん)- Contact '] | この{配線}{図}の{図}{記号}から、この{工事}で{使用}されていない{スイッチ}は。 ただし、{写真}下の{図}は、{接点}の{構成}を{示す}。 | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D |  | 2021_1,