## Sheet1
no | Eng | Picture | Option_1_Eng | Option_2_Eng | Option_3_Eng | Option_4_Eng | Ans | Vocab | Jpn | Option_1_Jpn | Option_2_Jpn | Option_3_Jpn | Option_4_Jpn | Exp | comment
1 | In the circuit shown in the figure, the power consumption [W] with an 8Ω resistor is. | Picture_1 | 200 | 800 | 1200 | 2000 | 2 | ['消費電力(しょうひでんりょく)- Electricity consumption', '抵抗(ていこう)- Resistor', '回路(かいろ)- Circuit'] | {図}のような{回路}で、8Ωの抵抗での消費{電力}[W]は。 | 200 | 800 | 1200 | 2000 | 1/20 + 1/30 = 5/60 This reciprocal is 60/5 = 12Ω. 12 + 8 = 20Ω. I=E/R = 200/20 = 10[A] P = IE = 10 x 200 = 2000 [W] 8:20=x:2000 20x = 16000 x = 800 [W] | 2021_2,
2 | The copper conductor of the same material with the closest resistance value to the copper conductor with a diameter of 2.6 mm and a length of 20 m |  | Cross-sectional area 8mm2, length 40m | Cross-sectional area 8mm2, length 20m | Cross-sectional area 5.5mm2, length 40m | Cross-sectional area 5.5mm2, length 20m | 4 | ['導線(どうせん)- Conducting wire', '銅(どう)- Copper', '直径(ちょっけい)- Diameter'] | {直径}2.6mm、{長さ}20mの銅{導線}と抵抗{値}が最も近い同{材質}の銅{導線}は。 | {断面積}8mm2、{長さ}40m | {断面積}8mm2、{長さ}20m | {断面積}5.5mm2、{長さ}40m | {断面積}5.5mm2、{長さ}20m |  | 2021_2,
3 | What is the calorific value [kJ] when using an electric heater with power consumption of 400 W for 1 hour and 20 minutes? |  | 960 | 1920 | 2400 | 2700 | 2 | ['時の(とき)- On time', '電熱器(でんねつき)- Electrothermic equipment'] | 消費{電力}が400Wの{電熱器}を1時間20分{使用}した時の{発熱量}[kJ]は。 | 960 | 1920 | 2400 | 2700 | Energy = Heat = 400 [W] x 1 hour 20 minutes = 400 [W] x (60 + 20) x 60 [s] = 1920,000 [W s] = 1920,000 [J] = 1920 [kJ] | 2021_2,
4 | In the circuit shown in the figure, when the power supply voltage is 24V, the current flowing through the resistor R = 4Ω is 6A, and the current flowing through the reactance XL = 3Ω is 8A, the power factor [%] of the circuit is. | Picture_4 | 43 | 60 | 75 | 80 | 2 | ['力率(りきりつ)- Power factor', '電源(でんげん)- Electrical power', '回路(かいろ)- Circuit'] | {図}のような{回路}で、{電源}{電圧}が24V、抵抗R=4Ωに{流れる}{電流}が6A、リアクタンスXL=3Ωに{流れる}{電流}が8Aであるとき、{回路}の{力率}[％]は。 | 43 | 60 | 75 | 80 |  | 2021_2,
5 | What is the current flowing through the three-phase three-wire circuit as shown in the figure? | Picture_5 | 2.9 | 5 | 5.8 | 10 | 3 | ['電流(でんりゅう)- Electric current', '回路(かいろ)- Circuit', '三相(さんそう)- Three phases'] | {図}のような{単相}2線式{回路}で、c-c’間の{電圧}が100Vのとき、a-a’間の{電圧}[V]は。 ただし、γ1及びγ2は{電線}の{電気}抵抗[Ω]とする。 | 2.9 | 5 | 5.8 | 10 | By transforming E=√3V V=E/√3=200/1.73…=115.61 I＝V/R = 115.61/20 = 5.78 ≒5.8[A] | 2021_2,
6 | In a single-phase two-wire circuit as shown in the figure, when the voltage between c and c'is 100V, the voltage [V] between a and a'is. However, γ1 and γ2 are the electrical resistance [Ω] of the electric wire. | Picture_6 | 101 | 102 | 103 | 104 | 2 | ['電圧(でんあつ)- Voltage', '回路(かいろ)- Circuit', '電線(でんせん)- Electric cable'] | {図}のような{単相}2線式{回路}で、c-c’間の{電圧}が100Vのとき、a-a’間の{電圧}[V]は。 ただし、γ1及びγ2は{電線}の{電気}抵抗[Ω]とする。 | 101 | 102 | 103 | 104 | 5 [A] + 5 [A] = 10 [A]. 2 x 0.05 [Ω] x 10 [A] = 1 [V]. 2 x 0.1 [Ω] x 5 [A] = 1 [V]. 1 [V] + 1 [V] + 100 [V] = 102 [V] | 2021_2,
7 | In the single-phase three-wire circuit shown in the figure, the two loads with a power consumption of 100 W and 200 W are both resistive loads. What is the voltage [V] between a and b when the wire is broken at the point marked with an x in the figure? However, it is assumed that the resistance value of the load does not change due to disconnection. | Picture_7 | 67 | 100 | 133 | 150 | 3 | ['断線(だんせん)- Disconnection', '負荷(ふか)- Load', '回路(かいろ)- Circuit'] | {図}のような{単相}3線式{回路}において、消費{電力}100W、200Wの2つの{負荷}はともに抵抗{負荷}である。{図}中の×印点で{断線}した{場合}、a-b間の{電圧}[V]は。 ただし、{断線}によって{負荷}の抵抗{値}は変化しないものとする。 | 67 | 100 | 133 | 150 | The current I flowing through the entire circuit is I = E/R = 200/150 = 1.333[A] The voltage between a and b is, E=IR=1.333…×100 = 133.333… ≒133[V] | 2021_2,
8 | What is the allowable current [A] per wire when six 600V vinyl insulated wires (annealed copper wire) with a diameter of 1.6mm are placed in the pipe for low-voltage indoor wiring work using metal pipes? However, the ambient temperature should be 30°C or less, and the current reduction factor should be 0.56. |  | 15 | 19 | 20 | 27 | 1 | ['許容(きょよう)- Permission', '直径(ちょっけい)- Diameter', '工事(こうじ)- Construction work', '低圧(ていあつ)- Low voltage'] | {金属}管による{低圧}{屋内配線}{工事}で、{管内}に{直径}1.6mmの600Vビニル{絶縁}{電線}（軟{銅線}）6本を収めて{施設}した{場合}、{電線}1本{当たり}の{許容}{電流} [A]は。 ただし、{周囲}{温度}は30°C{以下}、{電流}{減少}{係数}は0.56とする。 | 15 | 19 | 20 | 27 | Thickness Allowable current value 1.6mm 27A 2.0mm 35A 2.6mm 48A Therefore, 27A x 0.56 = 15.12A. | 2021_2,
9 | As shown in the figure, when branching a low-voltage indoor circuit with a VVR cable from a low-voltage indoor trunk line protected by a circuit breaker with a rated current of 100A, the combination of the length L between a and b and the wire thickness A is inappropriate. What it is. However, the relationship between VVR cable thickness and allowable current should be as shown in the table. | Picture_9 | L:1m A:2.0mm | L:2m A:5.5mm2 | L:10m A:8mm2 | L:15m A:14mm2 | 3 | ['太い(ふと)- Fat; thick', '電流(でんりゅう)- Electric current', '定格(ていかく)- Rated value'] | {図}のように、{定格}{電流}100Aの{配線}用{遮断器}で保護された{低圧}{屋内}{幹線}からVVRケーブルで{低圧}{屋内}{電路}を{分岐}する{場合}、a-b間の{長さ}Lと{電線}の太さAの{組合せ}として、{不適切}なものは。 ただし、VVRケーブルの太さと{許容}{電流}の関係は表のとおりとする。 | L:1m A:2.0mm | L:2m A:5.5mm2 | L:10m A:8mm2 | L:15m A:14mm2 |  | 2021_2,
10 | In the design of branch circuits for low-voltage indoor wiring, what is inappropriate as a combination of circuit breakers for wiring, wire thickness of branch circuits, and outlets? However, the distance from the branch point to the circuit breaker for wiring is 3 m, and the distance from the circuit breaker for wiring to the outlet is 8 m. Furthermore, the outlet must not be dual-purpose. |  | Picture_10_A | Picture_10_B | Picture_10_C | Picture_10_D | 2 | ['兼用(けんよう)- Multi-use; combined use', '分岐点(ぶんきてん)- Branch point', '低圧(ていあつ)- Low voltage'] | {低圧}{屋内配線}の{分岐}{回路}の{設計}で、配線用{遮断器}、{分岐}{回路}の{電線}の太さ及び{コンセント}の{組合せ}として、{不適切}なものは。 ただし、{分岐}点から配線用{遮断器}までは3m、配線用{遮断器}から{コンセント}までは8mとし、{電線}の{数値}は{分岐}{回路}の{電線}（軟{銅線}）の太さを{示す}。また、{コンセント}は{兼用}{コンセント}ではないものとする。 | Picture_10_A | Picture_10_B | Picture_10_C | Picture_10_D |  | 2021_2,
11 | Which of the following statements about "unthreaded box connectors" used in metal pipe work is incorrect? |  | There is a terminal for grounding to connect the bond wire. | Used to connect threadless conduits and metal outlet boxes. | When connecting to a threadless conduit, turn the set screw and tighten it so that the head of the screw is not threaded. | Use with an insulating bushing attached. | 3 | ['絶縁(ぜつえん)- Insulation', '接続(せつぞく)- Connection', '金属製(きんぞくせい)- Made of metal', '端子(たんし)- Terminal', '記述(きじゅつ)- Description'] | {金属}{管}{工事}に{使用}される「ねじなしボックス{コネクタ}」に関する{記述}として、誤っているものは。 | ボンド{線}を{接続}するための{接地}用の{端子}がある。 | ねじなし{電線}{管}と{金属}製アウトレットボックスを{接続}するのに用いる。{使用}する。 | ねじなし{電線}{管}との{接続}は止めネジを回して、ネジの頭部をねじ切らないように締め付ける。 | {絶縁}ブッシングを取り付けて |  | 2021_2,
12 | What is the maximum permissible temperature [°C] of insulation for 600V vinyl insulated wires (IV) used as low-voltage indoor wiring? |  | 45 | 60 | 75 | 90 | 2 | ['許容(きょよう)- Allowance', '電線(でんせん)- Cable', '低圧(ていあつ)- Low voltage'] | {低圧}{屋内配線}として{使用}する600Vビニル{絶縁}{電線}（IV）の{絶縁}{物の}最高{許容}{温度}[℃]は。 | 45 | 60 | 75 | 90 |  | 2021_2,
13 | What is the appropriate combination of materials and tools for attaching metal pipes to concrete walls? |  | Curl plug, staple, horso, hammer | Saddle, vibration drill, curl plug, wood screw | Chisels, concrete nails, hammers, staples | Bolt, horso, vibration drill, saddle | 2 | ['金属(きんぞく)- Metal', '材料(ざいりょう)- Materials'] | コンクリート{壁}に{金属}{管}を取り付けるときに用いる{材料}及び{工具}の{組合せ}として、{適切}なものは。 | カール{プラグ}、ステープル、ホルソ、ハンマ | サドル、{振動}ドリル、カール{プラグ}、木ねじ | たがね、コンクリート釘、ハンマ、ステープル | ボルト、ホルソ、{振動}ドリル、サドル |  | 2021_2,
14 | A three-phase induction motor is operated without load with a power supply frequency of 60Hz. What is the state of rotation when this motor is run without load with a power supply of frequency 50Hz? |  | Rotational speed does not change. | No rotation. | Rotational speed decreases. | Rotational speed increases. | 3 | ['低圧(ていあつ)- Low voltage', '速度(そくど)- Velocity', '回転(かいてん)- Rotation', '負荷(ふか)- Load', '電源(でんげん)- Power'] | {三相}{誘導電動機}が{周波数}60Hzの{電源}で無{負荷}運転されている。この電動機を{周波数}50Hzの{電源}で無{負荷}運転した{場合}の{回転}の{状態}は。 | {回転}{速度}は変化しない。 | {回転}しない。 | {回転}{速度}が{減少}する。 | {回転}{速度}が{増加}する。 |  | 2021_2,
15 | What is the purpose of connecting a low-voltage phase-advancing capacitor in parallel to a low-voltage three-phase induction motor? |  | Improve the power factor of the circuit. | Prevent motor vibration. | Prevent power frequency fluctuations. | Prevent fluctuations in rotation speed. | 1 | ['速度(そくど)- Velocity', '振動(しんどう)- Oscillation', '周波数(しゅうはすう)- Frequency', '回転(かいてん)- Rotation'] | {低圧}{三相}{誘導電動機}に対して{低圧}進相コンデンサを{並列}に{接続}する{目的}は。 | {回路}の{力率}を改善する。 | {電動機}の{振動}を防ぐ。 | {電源}の{周波数}の変動を防ぐ。 | {回転}{速度}の変動を防ぐ。 |  | 2021_2,
16 | What is the name of the material indicated by the arrow in the photo? | Picture_16 | Metal duct | Cable rack | Lighting duct | Type 2 metal wire | 2 | ['材料(ざいりょう)- Materials', '金属(きんぞく)- Metal', '矢印(やじるし)- Arrow (symbol)'] | {写真}の{矢印}で{示す}{材料}の{名称}は。 | {金属}ダクト | ケーブルラック | ライティングダクト | 2{種}{金属}製{線}ぴ |  | 2021_2,
17 | What is the use of the equipment shown in the photo? | Picture_17 | Used to project a reference line for attaching equipment, etc. | Used to measure illuminance. | Ued to check the degree of vibration. | Used as lighting in the work area. | 1 | ['写真(しゃしん)- Photography'] | {写真}に{示す}{器具}の{用途}は。 | {器具}等を取り付けるための基準{線}を投影するために用いる。 | {照度}を{測定}するために用いる。 | {振動}の度合いを確かめるために用いる。 | {作業}{場所}の照明として用いる。 |  | 2021_2,
18 | What is the use of the tool shown in the photo in electrical work? | Picture_18 | Used for bending hard vinyl chloride conduits. | Used for bending metal pipes (steel conduits). | Used for bending synthetic resin flexible conduits. | Used for bending lighting ducts. | 1 | ['曲げ(ま)- Flexure', '硬質(こうしつ)- Hardness', '電気工事(でんきこうじ)- Electrical work'] | {写真}に{示す}{工具}の{電気}{工事}における{用途}は。 | {硬質}塩化ビニル{電線}{管}の曲げ加工に用いる。 | {金属}{管}（{鋼製}{電線}{管}）の曲げ加工に用いる。 | {合成}樹脂製可とう{電線}{管}の曲げ加工に用いる。 | ライティングダクトの曲げ加工に用いる。 |  | 2021_2,
19 | There were the following points in the mutual connection of insulated wires in single-phase 100V indoor wiring work. What is the correct combination of all the appropriate ones selected from a to d? a: Fully covered with an insulating material that has an insulating effect equal to or greater than that of the electric wire. b: The tensile strength of the wire decreased by 10%. c: The electrical resistance of the wire increased by 5%. d: Did not increase the electric resistance of the wire. |  | aのみ | b及びc | b及びd | a, b及びd | 4 | ['絶縁(ぜつえん)- Insulation', '強さ(つよ)- Strength', '電線(でんせん)- Electric cable', '単相(たんそう)- Single phase'] | {単相}100Vの{屋内配線}{工事}における{絶縁}{電線}{相互}の{接続}で、次のような{箇所}があった。a～dのうちから{適切}なものを{全て}選んだ{組合せ}として、{正しい}ものは。 a：{電線}の{絶縁}物と同等以上の{絶縁}{効力}のあるもので十分に{被覆}した。 b：{電線}の引張{強さ}が10%{減少}した。 c：{電線}の{電気}抵抗が5%{増加}した。 d：{電線}の{電気}抵抗を{増加}させなかった。 | aのみ | b及びc | b及びd | a, b及びd |  | 2021_2,
20 | What is inappropriate as a construction method for low-voltage indoor wiring with a working voltage of 300 V or less? |  | In flexible metal conduit work, stranded wires (600V vinyl insulated wires) were used, and were housed without connecting parts inside the pipe. | In the lighting duct work, the opening of the duct was installed facing downward. | During the synthetic resin pipe work, the low-voltage wiring to be installed was in contact with the water pipe. | When branching electric wires in metal duct construction, the joints were covered with sufficient insulation, and the joints were placed in the duct so that they could be easily inspected. | 3 | ['点検(てんけん)- Inspection', '接続(せつぞく)- Connection', '方法(ほうほう)- Method', '電圧(でんあつ)- Voltage'] | {使用}{電圧}300V{以下}の{低圧}{屋内配線}の{工事}{方法}として、{不適切}なものは。 | {金属}可とう{電線}管{工事}で、{より線}（600Vビニル{絶縁}{電線}）を用いて、{管内}に{接続}{部分}を設けないで収めた。 | ライティングダクト{工事}で、ダクトの開口部を下に向けて{施設}した。 | {合成}樹脂{管}{工事}で、{施設}する{低圧}{配線}と水{管}が{接触}していた。 | {金属}ダクト{工事}で、{電線}を{分岐}する{場合}、{接続}{部分}に十分な{絶縁}{被覆}を施し、かつ、{接続}{部分}を{容易}に{点検}できるようにしてダクトに収めた。 |  | 2021_2,
21 | The circuit of the switch box is part of the construction of general low-voltage indoor wiring shown in the figure. However, (a) shows the ungrounded wire from the power supply (black), (b) shows the grounded wire from the power supply (white), and the load is directly connected to the grounded wire from the power supply. In addition, the pilot lamp uses the one for 100V. | Picture_21 | Picture_21_A | Picture_21_B | Picture_21_C | Picture_21_D | 2 | ['回路(かいろ)- Circuit', '低圧(ていあつ)- Low voltage', '結線(けっせん)- Hard wiring', '電源(でんげん)- Electrical power'] | {図}に{示す}{一般的}な{低圧}{屋内配線}の{工事}で、{スイッチ}ボックス{部分}の{回路}は。ただし、（a）は{電源}からの非{接地}側{電線}（黒色）、（b）は{電源}からの{接地}側{電線}（白色）を示し、{負荷}には{電源}からの{接地}側{電線}が{直接}に{結線}されているものとする。 なお、パイロットランプは100V用を{使用}する。 | Picture_21_A | Picture_21_B | Picture_21_C | Picture_21_D |  | 2021_2,
22 | For items that cannot be omitted, class D grounding work. However, it is assumed that the circuit is equipped with an earth leakage breaker with a rated sensitivity current of 30 mA and an operating time of 0.1 second. |  | 4m long metal pipe containing three-phase 200V (voltage to ground 200V) power wiring installed in a dry location | A three-phase 200 V (200 V to ground) induction motor pedestal installed to handle on a dry wooden floor. | The metal outer casing of a three-phase 200V room air conditioner installed on a dry concrete floor. | An 8m-long metal tube containing electric wires for single-phase three-wire 100/200V (voltage to ground 100V) wiring installed in a dry location. | 3 | ['長さ(なが)- Length', '配線(はいせん)- Wiring', '床(ゆか)- Floor', '木製(もくせい)- Wooden', '定格(ていかく)- Rated value', '省略(しょうりゃく)- Omission'] | D{種}{接地}{工事}を{省略}できないものは。 ただし、{電路}には{定格}{感度}{電流}30mA、{動作時間}0.1秒の{漏電}{遮断器}が取り付けられているものとする。 | 乾燥した{場所}に{施設}する{三相}200V（{対地}{電圧}200V）動力{配線}を収めた{長さ}4mの{金属}{管}。 | 乾燥した木製の{床}の上で取り扱うように{施設}する{三相}200V（{対地}{電圧}200V）{誘導電動機}の鉄台。 | 乾燥したコンクリートの{床}に{施設}する{三相}200V（{対地}{電圧}200V）ルームエアコンの{金属}製{外箱}{部分}。 | 乾燥した{場所}に{施設}する{単相}3線式100/200V（{対地}{電圧}100V）{配線}の{電線}を収めた{長さ}8mの{金属}{管}。 |  | 2021_2,
23 | When using a 600V vinyl insulated wire in a synthetic resin pipe for low-voltage indoor wiring work, the current reduction factor for obtaining the allowable current of the wire is a combination of the number of wires in the same pipe and the current reduction factor of the wire. , what is wrong. However, the ambient temperature should be 30°C or less. |  | 2本 0.80 | 4本 0.63 | 5本 0.56 | 7本 0.49 | 1 | ['電流(でんりゅう)- Electric current', '周囲温度(しゅういおんど)- Ambient temperature', '係数(けいすう)- Coefficient', '場合(ばあい)- Case', '低圧(ていあつ)-Low voltage'] | {低圧}{屋内配線}{工事}で、600Vビニル{絶縁}{電線}を{合成}樹脂管に収めて{使用}する{場合}、その{電線}の{許容}{電流}を求めるための{電流}{減少}{係数}{に関して}、同一{管内}の{電線}数と{電線}の{電流}{減少}{係数}との{組合せ}で、誤っているものは。 ただし、{周囲}{温度}は30°C{以下}とする。 | 2本 0.80 | 4本 0.63 | 5本 0.56 | 7本 0.49 |  | 2021_2,
24 | What is the wrong combination of measuring instruments and their uses when testing low-voltage circuits? |  | Circuit meter (tester) and continuity test | Phase detector and confirmation of the phase order (phase rotation) of the three-phase circuit | Power meter and power consumption measurement | Clamp-type ammeter and load current measurement | 3 | ['回路(かいろ)- Circuit', '電力計(でんりょくけい)- Wattmeter', '確認(かくにん)- Confirmation', '回路(かいろ)- Circuit'] | {低圧}{回路}を試験する{場合}の{測定}器とその{用途}の{組合せ}として、誤っているものは。 | {回路}計（テスタ） と {導通}試験 | 検相器 と {三相}{回路}の相順（相{回転}）の{確認} | {電力}計 と 消費{電力}量の{測定} | クランプ式{電流}計 と {負荷}{電流}の{測定} |  | 2021_2,
25 | What is wrong about insulation resistance measurement using an analog insulation resistance tester (with built-in battery)? |  | Before measuring insulation resistance, check that the battery capacity of the insulation resistance meter is normal. | Before the insulation resistance measurement, switch to the insulation resistance measurement range, enter the measurement mode, short the ground terminal (E: ground) and the line terminal (L: line), and confirm that the zero point is indicated. | When measuring the insulation of a circuit to which electronic equipment is connected, select an appropriate rated measurement voltage that will not damage the equipment. | Measure with the power supply voltage applied to the circuit under test. | 4 | ['測定(そくてい)- Measurement', '状態(じょうたい)- State; condition', '端子(たんし)- Terminal (electricity)', '前に(まえ)- Before'] | アナログ形{絶縁}抵抗計（{電池}内蔵）を用いた{絶縁}抵抗{測定}に関する{記述}として、誤っているものは。 | {絶縁}抵抗{測定}の前には、{絶縁}抵抗計の{電池}{容量}が正常であることを{確認}する。 | {絶縁}抵抗{測定}の前には、{絶縁}抵抗{測定}のレンジに切り替え、{測定}モードにし、{接地}{端子}（E:{アース}）と{線}路{端子}（L:ライン）を短絡し零点を指{示す}ることを{確認}する。 | 電子{機器}が{接続}された{回路}の{絶縁}{測定}を行う{場合}は、{機器}等を{損傷}させない適正な{定格}{測定}{電圧}を選定する。 | 被{測定}{回路}に{電源}{電圧}が加わっている{状態}で{測定}する。 |  | 2021_2,
26 | Equipped with a device that automatically cuts off the electric circuit in 0.1 seconds in the event of a ground fault on the low-voltage circuit with a working voltage of 100V. There is a vending machine that requires Class D grounding work outside of this electric circuit. The combination of the ground resistance value a [Ω] and the insulation resistance value b [MΩ] of the electric circuit does not conform to the "Ministerial Ordinance for Establishing Technical Standards for Electrical Equipment" and the "Interpretation of Technical Standards for Electrical Equipment". |  | a：600 b：2.0 | a：450 b：1.0 | a：200 b：0.2 | a：50 b：0.1 | 1 | ['種(たね)- Seed', '解釈(かいしゃく)- Interpretation', '屋外(おくがい)- Outdoors', '装置(そうち)- Equipment', '使用(しよう)- use; application'] | {使用}{電圧}100Vの{低圧}{電路}に、地絡が生じた{場合}0.1秒で{自動}的に{電路}を{遮断}する装置が施してある。この{電路}の{屋外}に D{種}{接地}{工事}が{必要}な{自動}{販売}機がある。その{接地}抵抗{値}a[Ω]と{電路}の{絶縁}抵抗{値}b[MΩ]の{組合せ}として、「{電気}{設備}に関する{技術基準}を定める{省令}」及び「{電気}{設備}の{技術基準}の{解釈}」に適合していないものは。 | a：600 b：2.0 | a：450 b：1.0 | a：200 b：0.2 | a：50 b：0.1 |  | 2021_2,
27 | What are the incorrect descriptions of the characteristics of analog and digital instruments? |  | Analog gauges, like permanent magnet moving coil type gauges, use electromagnetic force to move the pointer and read the value from the scale based on the contact angle. | A digital instrument converts an analog waveform such as an AC voltage applied to a measurement input terminal into a DC voltage in an input conversion circuit, then sends it to an A-D conversion circuit, converts the DC voltage into a digital quantity according to its magnitude, and measures it. value is displayed. | Analog instruments are easy to read the degree of change and have the advantage of being able to intuitively judge the measured quantity, but they are prone to reading errors. | In voltage measurement, an analog meter has a high input resistance and does not easily affect the circuit under test, whereas a digital meter has a low input resistance and thus tends to affect the circuit under test. | 4 | ['直流(ちょくりゅう)- Direct current', '指針(ししん)- Needle (compass, gauge, etc.)', '特徴(とくちょう)- Characteristic', '計器(けいき)- Meter; gauge'] | アナログ{計器}とディジタル{計器}の特徴に関する{記述}として、誤っているものは。 | アナログ{計器}は永久磁石{可動}{コイル}形{計器}のように、{電磁}力等で指針を動かし、触れ角でスケールから{値}を読み取る。 | ディジタル{計器}は{測定}入力{端子}に加えられた{交流}{電圧}などのアナログ波形を入力変換{回路}で{直流}{電圧}に変換し、次にA-D変換{回路}に送り、{直流}{電圧}この大きさに応じたディジタル量に変換し、{測定}{値}が{表示}される。 | アナログ{計器}は変化の度合いを読み取りやすく、{測定}量を直感的に{判断}できる利点を持つが、読み取り誤差を生じやすい。 | {電圧}{測定}では、アナログ{計器}は入力抵抗が{高い}ので被{測定}{回路}に影響を与えにくいが、ディジタル{計器}は入力抵抗が低いので被{測定}{回路}に影響を与えやすい。 |  | 2021_2,
18 | According to the "Electrical Construction Professionals Act", for construction work related to general electric facilities, both a and b can only be engaged in by electricians. |  | a: Attach the switchboard to the construction material. b: Bend the conduit. | a: Install pipes for underground cables. b: Install a power meter with a rated voltage of 100V. | a: Install poles to support the wires. b: Put the electric wire in the conduit. | a: Bury the ground electrode in the ground. b: Connect the cord to the plug connector with a rated voltage of 125V. | 1 | ["地面(じめん)- Earth's surface", '定格(ていかく)- Rated value', '従事(じゅうじ)- Engaging in ', '作業(さぎょう)- Work', '作物(さくもつ)- Farm products', '電気工(でんきこう)- Electrician'] | 「{電気}{工事}士法」において、一般用{電気}工{作物}に係る{工事}の{作業}で、a, bともに{電気}{工事}士でなければ{従事}できないものは。 | a：{配電盤}を造営材に取り付ける。 b：{電線}{管}を曲げる。 | a：{地中}{電線}用の{管}を{設置}する。 b：{定格}{電圧}100Vの{電力}量計を取り付ける。 | a：{電線}を支持する柱を{設置}する。 b：{電線}{管}に{電線}を収める。 | a：{接地}{極}を地面に埋設する。 b：{定格}{電圧}125Vの差込み{接続}器にコードを{接続}する。 |  | 2021_2,
29 | Which of the following statements about the "Electrical Appliance and Material Safety Law" is correct? |  | Electrical workers shall not use electrical equipment for construction work such as installation of electrical facilities unless legally labeled. (excluding electrical equipment used). | Specified Electrical Appliances and Materials are marked with (mark below) or (PS)E. | Earth leakage breakers with a rated operating voltage of 100V are electrical appliances other than specified electrical appliances. | Any machine, apparatus or material that forms part of or is used in connection with an electrical work piece is an electrical article. | 1 | ['承認(しょうにん)- Recognition', '使用(しよう)- Use', '表示(ひょうじ)- Indication', '記述(きじゅつ)- Description; account'] | 「{電気}{用品}安全法」について述べた{記述}で、{正しい}ものは。 | {電気}{工事}士は、適法な{表示}が付されているものでなければ、{電気}{用品}を{電気}工{作物}の{設置}等の{工事}に{使用}してはならない（経済産業大臣の承認を受けた{特定}の{用途}に{使用}される{電気}{用品}を除く）。 | {特定}{電気}{用品}には、（下{図}のマーク)または（PS）Eの{表示}が付されている。 | {定格}{使用}{電圧}100Vの{漏電}{遮断器}は{特定}{電気}{用品}以外の{電気}{用品}である。 | {電気}工{作物}の{部分}となり、又はこれに{接続}して用いられる{機械}、{器具}又は、{材料}はすべて{電気}{用品}である。 |  | 2021_2,
30 | Which is the correct AC voltage category specified in the "Ministerial Ordinance for Establishing Technical Standards for Electrical Equipment"? |  | Low voltage is 600V or less, high voltage is over 600V and 10000V or less | Low voltage is 600V or less, high voltage is over 600V and 7000V or less | Low voltage is 750V or less, high voltage is over 750V and 10000V or less | Low voltage is 750V or less, high voltage is more than 750V and less than 7000V | 2 | ['省令(しょうれい)- Ministerial ordinance', '高圧(こうあつ)- High voltage', '交流(こうりゅう)- Exchange'] | 「{電気}{設備}に関する{技術基準}を定める{省令}」で定められている{交流}の{電圧}区分で、{正しい}ものは。 | {低圧}は600V{以下}、{高圧}は600Vを超え10000V{以下} | {低圧}は600V{以下}、{高圧}は600Vを超え7000V{以下} | {低圧}は750V{以下}、{高圧}は750Vを超え10000V{以下} | {低圧}は750V{以下}、{高圧}は750Vを超え7000V{以下} |  | 2021_2,
31 | What is the minimum height [m] above the ground surface of the spur line attachment point indicated by ①? However, the service line must not cross the road, must be technically unavoidable, and must not obstruct traffic. |  | 2 | 2.5 | 3 | 4 | 2 | ['支障(ししょう)- Obstacle', '道路(どうろ)- Road', '高さ(たか)- Height'] | ①で{示す}引込{線}取付点の地表上の{高さ}の最低{値}[m]は。 ただし、引込{線}は{道}路を横断せず、技術上やむを得ない{場合}で、交通に支障がないものとする。 | 2 | 2.5 | 3 | 4 |  | 2021_2,
32 | The symbols (types) of wires that cannot be used for wiring work shown in ② are |  | VVF | VVR | IV | CV | 3 | ['記号(きごう)- Sign', '電線(でんせん)- Electric cable', '使用(しよう)- Use'] | ②で{示す}{配線}{工事}に{使用}できない{電線}の{記号}（{種類}）は。 | VVF | VVR | IV | CV |  | 2021_2,
33 | What is the type of equipment for the symbol shown in ③? |  | Hot wire automatic switch | Delay switch | Flasher with built-in confirmation indicator light | Flasher with built-in position indicator light | 4 | ['点滅器(てんめつき)- Switch', '自動(じどう)- Automatic', '種類(しゅるい)- Kind; type'] | ③で{示す}{図}{記号}の{器具}の{種類}は。 | 熱{線}式{自動}{スイッチ} | {遅延}{スイッチ} | {確認}{表示}灯を内蔵する{点滅器} | {位置}{表示}灯を内蔵する{点滅器} |  | 2021_2,
34 | Equipment with the symbol shown in ④. |  | Box switch with ammeter | Low-voltage phase-advancing capacitor to improve the power factor of the motor | Switch (electromagnetic switch) operated by control wiring signals | Motor starter | 3 | ['装置(そうち)- Equipment; device', '制御(せいぎょ)- Control', '力率(りきりつ)- Power factor', '電動機(でんどうき)- Electric motor', '画像(がぞう)- Image'] | ④で{示す}{図}{記号}の{機器}は。 | {電流}計付箱{開閉器} | {電動機}の{力率}を改善する{低圧}進相用コンデンサ | 制御{配線}の信号により動作する{開閉器}（{電磁}{開閉器}） | {電動機}の{始動}装置 |  | 2021_2,
35 | What is the maximum value [A] of the rated current of the equipment shown in ⑤? |  | 15 | 20 | 25 | 30 | 4 | ['電流(でんりゅう)- Electric current', '定格(ていかく)- Rated value', '機器(きき)- Device'] | ⑤で{示す}{機器}の{定格}{電流}の{最大値}[A]は。 | 15 | 20 | 25 | 30 |  | 2021_2,
| What is the name of the instrument with the graphical symbol shown in ⑥? |  | Remote control relay | Remote control selector switch | Fire indicator light | Earth leakage alarm | 1 | ['漏電(ろうでん)- Short circuit', '問題(もんだい)- Question', '器具(きぐ)- Tool; instrument'] | ⑥で{示す}{図}{記号}の{器具}の{名称}は。 | リモコン{リレー} | リモコンセレクタ{スイッチ} | 火災{表示}灯 | {漏電}{警報器} |  | 2021_2,
37 | What is the permissible maximum value [Ω] of grounding resistance in the grounding work of the part indicated by ⑦? There is no ground fault interrupter installed on the power supply side of the service line. |  | 10 | 100 | 300 | 500 | 2 | ['装置(そうち)- Equipment', '遮断(しゃだん)- Isolation', '抵抗(ていこう)- Resistance', '接地(せっち)- Ground (electricity)', '部分(ぶぶん)- Section; part'] | ⑦で{示す}{部分}の{接地}{工事}における{接地}抵抗の{許容}される{最大値}[Ω]は。 なお、引込{線}の{電源}側には地絡{遮断}装置は{設置}されていない。 | 10 | 100 | 300 | 500 |  | 2021_2,
38 | What is the name of the instrument indicated by the symbol ⑧? |  | Push button for electromagnetic switch | Float switch | Pressure switch | Floatless switch electrode | 4 | ['楽器(がっき)- ', '記号(きごう)- Sign'] | ⑧で{示す}{図}{記号}の{器具}の{名称}は。 | {電磁}{開閉器}用押しボタン | フロート{スイッチ} | {圧力}{スイッチ} | フロートレス{スイッチ}電{極} |  | 2021_2,
39 | What is the minimum number of wires (number of cores) for the part indicated by ⑨? |  | 2 | 3 | 4 | 5 | 1 | ['本数(ほんすう)- Number ', '最少(さいしょう)- Fewest; least', '部分(ぶぶん)- portion'] | ⑨で{示す}{部分}の{最少}{電線}{本数}（心線数）は。 | 2 | 3 | 4 | 5 |  | 2021_2,
40 | The part indicated by ⑩ is a hook-type outlet. The sidenote indication of the graphic symbol is. |  | T | LK | EL | H | 1 | ['表示(ひょうじ)- Indication', '部分( ぶぶん)- Section; part'] | ⑩で{示す}{部分}は引掛形の{コンセント}である。 その{図}{記号}の傍記{表示}は。 | T | LK | EL | H |  | 2021_2,
41 | ⑪ The equipment with the symbol shown in |  | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D | 4 | ['機器(きき)- Device; equipment', '記号(きごう)- Sign '] | ⑪で{示す}{図}{記号}の{機器}は。 | Picture_41_A | Picture_41_B | Picture_41_C | Picture_41_D |  | 2021_2,
42 | If all the connections in the box shown in ⑫ are crimp connections, what is the correct combination of ring sleeve type and minimum number to be used? However, all electric wires to be used shall be VVF1.6, and the number of electric wires (core wires) for wiring to the first basement floor shall be minimized. |  | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D | 3 | ['最少(さいしょう)- Fewest; least', '種類(しゅるい)- Variety', '場合(ばあい)- Case; situation', '接続(せつぞく)- Connection '] | ⑫で{示す}ボックス内の{接続}をすべて{圧着}{接続}とする{場合}、{使用}するリングスリーブの{種類}と{最少}{個数}の{組合せ}で、{正しい}ものは。 ただし、{使用}する{電線}はすべてVVF1.6とし、地下1階へ至る{配線}の{電線}{本数}（心線数）は{最少}とする | Picture_42_A | Picture_42_B | Picture_42_C | Picture_42_D |  | 2021_2,
43 | What is not used in the pump room on the first basement floor indicated by ⑬. |  | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D | 3 | ['室内(しつない)- Indoor', '地下(ちか)- Underground'] | ⑬で{示す}地下1階のポンプ室内で{使用}されていないものは。 | Picture_43_A | Picture_43_B | Picture_43_C | Picture_43_D |  | 2021_2,
44 | What cables are necessary for the wiring work of the part indicated by ⑭? However, the number of core wires should be the minimum. |  | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D | 3 | ['本数(ほんすう)- Number', '最小限(さいしょうげん)- Minimum', '部分(ぶぶん)- Portion'] | ⑭で{示す}{部分}の{配線}{工事}に{必要}なケーブルは。ただし、心線数は{最少}とする。 | Picture_44_A | Picture_44_B | Picture_44_C | Picture_44_D |  | 2021_2,
45 | The construction of the part shown in ⑮ that is not generally used. |  | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D | 4 | ['工事(こうじ)- Construction work', '部分(ぶぶん)- Portion'] | ⑮で{示す}{部分}の{工事}で、{一般的}に{使用}されることのないものは。 | Picture_45_A | Picture_45_B | Picture_45_C | Picture_45_D |  | 2021_2,
46 | The construction of the part shown in ⑯, which is not generally used. |  | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D | 4 | ['一般的(いっぱんてき)- General', '工事(こうじ)- Construction work', '部分(ぶぶん)- Portion'] | ⑯で{示す}{部分}の{工事}で、{一般的}に{使用}されることのないものは。 | Picture_46_A | Picture_46_B | Picture_46_C | Picture_46_D |  | 2021_2,
47 | If all the connections in the box indicated by ⑰ are plug-in connectors, what is the correct combination of the type of plug-in connectors to be used and the minimum number? However, all electric wires to be used shall be VVF1.6, and the number of electric wires (core wires) for wiring to the first basement floor shall be minimized. |  | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D | 4 | ['心線(しんせん)- Conductor', '電線(でんせん)- Electric cable', '種類(しゅるい)- Variety; kind', '場合(ばあい)- Case; situation', '接続(せつぞく)- Connection'] | ⑰で{示す}ボックス内の{接続}をすべて差込形{コネクタ}とする{場合}、{使用}する差込形{コネクタ}の{種類}と{最少}{個数}の{組合せ}で、{正しい}ものは。 ただし、{使用}する{電線}はすべてVVF1.6とし、地下1階へ至る{配線}の{電線}{本数}（心線数）は{最少}とする。 | Picture_47_A | Picture_47_B | Picture_47_C | Picture_47_D |  | 2021_2,
48 | When the connection in the box shown in ⑱ is crimped with a ring sleeve, the type and number of ring sleeves, and the stamp after crimping connection, However, all wires used shall be VVF1.6. In addition, O, small, and medium in the center of the ring sleeve shown in the photo represent engravings. |  | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D | 1 | ['写真(しゃしん)- Photography', '電線(でんせん)- Cable', '個数(こすう)- Quantity', '種類(しゅるい)- variety; kind', '接続(せつぞく)- Connection'] | ⑱で{示す}ボックス内の{接続}をリングスリープで{圧着}{接続}した{場合}のリングスリーブの{種類}、{個数}及び{圧着}{接続}後の{刻印}との{組合せ}で、 ただし、{使用}する{電線}はすべてVVF1.6とする。また、{写真}に{示す}リングスリーブ{中央}のO、小、中は{刻印}を表す。 | Picture_48_A | Picture_48_B | Picture_48_C | Picture_48_D |  | 2021_2,
49 | From the symbol in this wiring diagram, the outlet used in this construction. |  | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D | 4 | ['構造(こうぞう)- Structure', '配線図(はいせんず)- Wiring diagram'] | この{配線}{図}の{図}{記号}から、この{工事}で{使用}されている{コンセント}は。 | Picture_49_A | Picture_49_B | Picture_49_C | Picture_49_D |  | 2021_2,
50 | From the symbols in this wiring diagram, which switch is not used in this construction? However, the diagram below the photo shows the configuration of the contacts. |  | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D | 4 | ['構成(こうせい)- Composition', '接点(せってん)- Contact', '記号(きごう)- Symbol; code', '配線図(はいせんず)- Wiring diagram'] | この{配線}{図}の{図}{記号}から、この{工事}で{使用}されていない{スイッチ}は。ただし、{写真}下の{図}は、{接点}の{構成}を{示す}。 | Picture_50_A | Picture_50_B | Picture_50_C | Picture_50_D |  | 2021_2,